## Sheet1
Date Filed | Company Name | Division Name | City/Town | Street Name | Substation | Circuit Number | KV Levels | Circuit Type | Original Customers Affected | Current Customers Affected | Actual Duration | Total Customer Outage Hrs | Date and Time Out | Date and Time In | Reason for Outage | Failed or Damaged Equipment | Planned Incident ID | Weather Condition | Load Type | Critical Facility Affected | Major Excludable Emergency | Injury | Filed By | Time Restoration Commenced | Expected Duration | Notifications | Official Notified Name (1) | Official Notified Phone (1) | Official Notified Name (2) | Official Notified Phone (2) | Comments | Contact Name | Contact Phone # | Parent Incident ID | Report Type
04/03/2026 09:25:04 | MECo | Bay State South | MILFORD | CENTRAL ST | DEPOT STREET 335 | 05-335W2 | 15 | OH | 21 | 0 | 4.53 | 95.08 | 02/23/2026 09:25 | 02/23/2026 13:57 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/23/2026 13:56 |  | N |  |  |  |  | Blown line fuse P34 Central St, cause unknown. Blizzard 2026. ABB Order Id: 871434 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8841096 | A
04/03/2026 09:23:55 | MECo | Bay State South | UPTON | WESTBORO ST | DEPOT STREET 335 | 05-335W3 | 15 | OH | 3 | 0 | 27.10 | 81.25 | 02/23/2026 09:10 | 02/24/2026 12:16 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | P33 Westboro St blown line fuse - P3 broken guy wire Eames St - tree limb fell - straightened pole. Three sections of primary and secondary down. Blizzard 2026. ABB Order Id: 871376 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810518 | A
04/03/2026 09:14:24 | MECo | Bay State South | UPTON | FOWLER EAST RD | DEPOT STREET 335 | 05-335W3 | 15 | OH | 1 | 0 | 13.75 | 33.05 | 02/23/2026 10:06 | 02/23/2026 20:38 | Tree Contact | Tap |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell around pole 8 Fowler Rd, pulled tap off primary, de-energized transformers at P4, manually opened line fuse P14 Fowler, made repairs, put phase back up. ABB Order Id: 871732, 872755, 872786 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810320 | A
04/03/2026 08:54:05 | MECo | Bay State South | MENDON | HARTFORD EAST AVE | MENDON 332 | 05-332W1 | 15 | OH | 94 | 0 | 1.89 | 177.03 | 02/25/2026 16:36 | 02/25/2026 18:30 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Found TripSaver cutout open (1 of 3) at P51 Hartford East, cause was tree took down primary P8 Neck Hill Rd. ABB Order Id: 874409 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811122 | A
04/03/2026 08:50:48 | MECo | Bay State South | REHOBOTH | TREMONT ST | REYNOLDS AVE 3323 | 05-3323L5 | 5 |  | 1 | 0 | 35.48 | 35.48 | 02/23/2026 10:01 | 02/24/2026 21:30 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse, tree fell and took down pole P4253-14 Tremont St. End of long driveway. Replace transformer and pole and services fixed. ABB Order Id: 873562, 871704 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810838 | A
04/03/2026 08:45:04 | MECo | Bay State South | ATTLEBORO | THURBER AVE | REYNOLDS AVE 3323 | 05-3323L5 | 15 | OH | 11 | 0 | 21.91 | 240.90 | 02/23/2026 07:45 | 02/24/2026 05:40 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P3991 Thurber Av. Cutout tap broke off from wind. Blizzard 2026. ABB Order Id: 871933 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810417 | A
04/03/2026 08:42:59 | MECo | Bay State South | REHOBOTH | TREMONT ST | REYNOLDS AVE 3323 | 05-3323L5 | 5 | OH | 1 | 0 | 20.48 | 20.48 | 02/23/2026 07:42 | 02/24/2026 04:11 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down pole and service drop to 464 Tremont St. ABB Order Id: 870976 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8841043 | A
04/03/2026 08:40:27 | MECo | Bay State South | REHOBOTH | ANAWAN ST | REYNOLDS AVE 3323 | 05-3323L4 | 5 | OH | 1 | 0 | 33.22 | 33.22 | 02/23/2026 07:36 | 02/24/2026 16:49 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 10:53 |  | N |  |  |  |  | Tree fell and took down service drop at 242 Anawan St. Also needs electrician. ABB Order Id: 870905 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8841042 | A
04/02/2026 10:52:58 | MECo | Bay State South | QUINCY | BILLINGS RD | ATLANTIC 4 | 07-4J2 | 5 | OH | 1 | 0 | 56.26 | 56.26 | 02/23/2026 11:25 | 02/25/2026 19:40 | Failed Equipment | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Replaced burnt up copper service to 199 Billings Rd. ABB Order Id: 874436, 872050 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811121 | A
04/02/2026 10:49:49 | MECo | Bay State South | QUINCY | HENRY ST | ATLANTIC 4 | 07-4J2 | 5 | OH | 79 | 0 | 11.33 | 894.89 | 02/23/2026 08:20 | 02/23/2026 19:40 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown B and C-phase line fuses (2 of 3) P8 Henry St. Cause: Unknown. ABB Order Id: 871148 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810312 | A
04/02/2026 10:43:02 | MECo | Bay State South | QUINCY | BILLINGS RD | ATLANTIC 4 | 07-4J2 | 5 | OH | 39 | 0 | 14.57 | 568.30 | 02/23/2026 05:40 | 02/23/2026 20:15 | Failed Equipment | Cutout - enclosed |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown A-phase line fuse (1 of 3) P29-90 Billings Rd. Cause: Failed enclosed porcelain riser cutout P12 Arnold Rd. ABB Order Id: 870255 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810311 | A
04/02/2026 10:28:35 | MECo | Bay State South | QUINCY | TIRRELL ST | ATLANTIC 4 | 07-4J1 | 5 | OH | 120 | 0 | 12.14 | 1456.63 | 02/23/2026 05:51 | 02/23/2026 18:00 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown A-phase line fuse (1 of 3) P9 Tirrell St. Cause: Broken tree limb on primary P14 Edgeworth Rd and took down service to 19 Edgeworth Rd. ABB Order Id: 872436, 870368, 872119 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810313 | A
04/02/2026 09:43:56 | MECo | Bay State South | RANDOLPH | UNION ST | RANDOLPH 5 | 07-5W4 | 15 | OH | 222 | 0 | 17.57 | 3899.62 | 02/23/2026 06:42 | 02/24/2026 00:53 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown C-phase line fuse (1 of 2) P41 Union St. Cause: Broken tree limb took down primary P25 Union St. ABB Order Id: 870599 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810372 | A
04/02/2026 09:38:41 | MECo | Bay State South | REHOBOTH | SCHOOL ST | REYNOLDS AVE 3323 | 05-3323L2 | 15 | OH | 3 | 0 | 16.05 | 48.14 | 02/23/2026 19:48 | 02/24/2026 11:51 | Unknown | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/24/2026 11:13 |  | N |  |  |  |  | Blown line fuse P2270 School St. Cause unknown. Blizzard 2026. ABB Order Id: 872905 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8841023 | A
04/02/2026 09:28:57 | MECo | Bay State South | REHOBOTH | POND ST | REYNOLDS AVE 3323 | 05-3323L2 | 5 | OH | 1 | 0 | 21.93 | 21.92 | 02/23/2026 13:12 | 02/24/2026 11:08 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Made repairs to service drop at 43 Pond St due to tree limb. ABB Order Id: 872325 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810495 | A
04/02/2026 09:27:13 | MECo | Bay State South | REHOBOTH | COUNTY ST | REYNOLDS AVE 3323 | 05-3323L2 | 15 | OH | 3 | 0 | 28.11 | 84.34 | 02/23/2026 12:31 | 02/24/2026 16:38 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P816 County St. Needed tree crew. Sleeved neutral together and reattached primary P816-2. ABB Order Id: 872209 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810685 | A
04/02/2026 09:27:13 | MECo | Bay State South | QUINCY | WASHINGTON ST | FIELD STREET 1 | 07-1W9 | 15 | OH | 150 | 0 | 13.25 | 1979.35 | 02/23/2026 04:25 | 02/23/2026 17:40 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown C-phase line fuse (1 of 3) P66 Washington St. Cause: Slack span of primary between P66 Washington St to P2 Massachusetts Ave during high wind event. Manually opened remaining fuses to pull slack. ABB Order Id: 870028, 872753, 872756 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810257 | A
04/02/2026 09:02:46 | MECo | Bay State South | REHOBOTH | ELM ST | REYNOLDS AVE 3323 | 05-3323L2 | 15 | OH | 5 | 0 | 31.34 | 156.72 | 02/23/2026 11:13 | 02/24/2026 11:17 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P1963 Elm St, crew said the fuse keeps blowing because the primary is sagging too much and slapping the neutral. Knock off ice and limbs and pulled slack. ABB Order Id: 873574 ABB Order Id: 872012 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810496 | A
04/02/2026 08:55:29 | MECo | Bay State South | REHOBOTH | RESERVOIR AVE | REYNOLDS AVE 3323 | 05-3323L2 | 5 | OH | 1 | 0 | 33.12 | 33.12 | 02/23/2026 08:49 | 02/24/2026 17:56 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell at 55 Reservoir Ave - 2 broken poles leading down driveway, wires down, also needs electrician. ABB Order Id: 871254 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810739 | A
04/02/2026 08:53:03 | MECo | Bay State South | REHOBOTH | WINTER ST | REYNOLDS AVE 3323 | 05-3323L2 | 5 | OH | 2 | 0 | 32.06 | 64.11 | 02/23/2026 08:02 | 02/24/2026 11:52 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 11:52 |  | N |  |  |  |  | Tree fell took down service drop to 10 Winter St. ABB Order Id: 871049, 873665 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8841020 | A
04/02/2026 08:49:54 | MECo | Bay State South | REHOBOTH | MOULTON ST | REYNOLDS AVE 3323 | 05-3323L2 | 15 | OH | 229 | 0 | 13.15 | 3010.78 | 02/23/2026 06:09 | 02/23/2026 19:28 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P5035 at corner of Kelton and Moulton St. Cause was various tree limbs down including P1870 Kelton St. Blizzard 2026. ABB Order Id: 870392 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810297 | A
04/02/2026 08:11:57 | MECo | Bay State South | MILLVILLE | CHESTNUT HILL RD | UXBRIDGE 321 | 05-321W9 | 15 | OH | 1 | 0 | 43.87 | 43.87 | 02/23/2026 07:23 | 02/25/2026 03:15 | Tree Contact | No failure or Unknown |  | NORM | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P46 Chestnut Hill Rd due to fallen tree branch between pole 46 to pole 46-1. ABB Order Id: 874051, 873799, 870842 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8841018 | A
04/02/2026 08:06:17 | MECo | Bay State South | MILLVILLE | CHESTNUT HILL RD | UXBRIDGE 321 | 05-321W9 | 15 | OH | 46 | 0 | 48.40 | 845.39 | 02/23/2026 09:37 | 02/24/2026 03:44 | Failed Equipment | Pole - wood |  | BLIZ | M | Y | Y | N | tc |  |  | Y | Bill Coupe;Peter Caruso; | Email (bill.coupe@millvillepolice.org);Email (townadmin@millvillema.org); |  |  | Manually opened line fuse P97 Chestnut Hill Rd to repair downed lines and replace P98 Chestnut Hill Rd. Blizzard 2026. Note: fuse is missing in GIS, only 45 customers were affected. ABB Order Id: 873103 Also, reattached service at house that was downed from tree to restore power. ABB Order Id: 873677 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810404 | A
04/02/2026 07:45:59 | MECo | Bay State South | UXBRIDGE | WEST 3 ST | UXBRIDGE 321 | 05-321W4 | 15 | OH | 1 | 0 | 25.69 | 28.97 | 02/23/2026 11:18 | 02/24/2026 09:43 | Failed Equipment | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | P20 West St broken in Blizzard 2026. Initially affected house 485 West St. Made safe, next morning opened line fuse P14 West St to replace P20. ABB Order Id: 872021, 873302 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810454 | A
04/02/2026 07:44:19 | MECo | Bay State South | BROCKTON | OAK ST | PARKVIEW SUB. | 07-94W41 | 15 |  | 1 | 0 | 30.02 | 30.02 | 02/23/2026 10:57 | 02/24/2026 16:58 | Physical Interference / Other | Transformer padmount |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 13:07 |  | N |  |  |  |  | Plow hit pad 62-1 Oak St. ABB Order Id: 871973 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840078 | A
04/01/2026 14:13:21 | MECo | Bay State South | REHOBOTH | PROVIDENCE ST | MINK STREET 7 | 05-7L4 | 15 | OH | 285 | 0 | 0.18 | 52.25 | 02/24/2026 18:05 | 02/24/2026 18:17 | Tree Contact | No failure or Unknown |  | NORM | M | Y | Y | N | tc |  |  | N |  |  |  |  | Manually opened line fuses P2016 Providence St, to remove tree on wires P717 County St, Seekonk. ABB Order Id: 873937 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810763 | A
04/01/2026 14:09:35 | MECo | Bay State South | SEEKONK | LAKE ST | MINK STREET 7 | 05-7L4 | 15 | OH | 20 | 0 | 19.73 | 394.33 | 02/23/2026 06:36 | 02/24/2026 02:20 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Found 1 of 3 TripSaver cutouts open at P907 Lake St. Pole to pole guy wire keeps making contact with primary at pole 2844 Summer St Rehoboth. Conductor welded to pole to pole guy wire so we out rigged primary to have clearance. ABB Order Id: 870593 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810395 | A
04/01/2026 13:42:21 | MECo | Bay State South | BELLINGHAM | CROSS ST | BEAVER POND 344 | 05-344W4 | 15 | OH | 1641 | 0 | 2.01 | 3294.76 | 02/23/2026 08:02 | 02/23/2026 10:02 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 10:05 |  | Y | Joseph Laydon;Bill Miller; | Email (jlaydon@bellinghamma.org);Email (bmiller@bellinghamma.org); |  |  | Pole top recloser locked out at P2 Cross St. Cause was tree limb across 3 phase between P10 and P11 Cross St. Blizzard 2026. ABB Order Id: 871050 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840909 | A
04/01/2026 13:29:27 | MECo | Bay State South | NORTON | WEST MAIN ST | NORTON 4 | 05-4L2 | 15 | OH | 2176 | 0 | 35.31 | 4575.70 | 02/23/2026 05:44 | 02/23/2026 07:48 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser lockout P2 off West Main St. Cause was tree branches on Reservoir St, Norton. Blizzard 2026. ABB Order Id: 870267 Blown line fuse P2929 Reservoir St. Primary broken. ABB Order Id: 871026 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810106 | A
04/01/2026 12:58:50 | MECo | Bay State South | BELLINGHAM | BOX POND RD | DEPOT STREET 335 | 05-335W1 | 15 | OH | 24 | 0 | 14.93 | 358.40 | 02/23/2026 09:04 | 02/24/2026 00:00 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P17 Box Pond Dr. Tree fell, broken pole at P31 Box Pond Dr. Truck broke down. Blizzard 2026. ABB Order Id: 872081 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810553 | A
04/01/2026 12:53:51 | MECo | Bay State South | MILFORD | 335W 1 LINE LINE | DEPOT STREET 335 | 05-335W1 | 15 | OH | 1951 | 0 | 1.60 | 3124.31 | 02/23/2026 09:49 | 02/23/2026 11:25 | Failed Equipment | Overhead Device Other |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | 335W1 feeder lockout at Little Depot Sub due to phases off insulators at poles 57 and 58 South Main St, Hopedale. Blizzard 2026. Customer count reduced by previously blown line fuse. ABB Order Id: 871591 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810139 | A
04/01/2026 12:43:43 | MECo | Bay State South | UXBRIDGE | CHESTNUT ST | UXBRIDGE 321 | 05-321W2 | 15 | OH | 1 | 0 | 8.70 | 8.70 | 02/23/2026 09:42 | 02/23/2026 18:25 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P45 Chestnut St. Tree fell between P45-1 and 45-2 Chestnut St. ABB Order Id: 871525 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810282 | A
04/01/2026 12:41:50 | MECo | Bay State South | MILLVILLE | CENTRAL ST | UXBRIDGE 321 | 05-321W2 | 5 | OH | 1 | 0 | 12.65 | 12.65 | 02/23/2026 06:57 | 02/23/2026 19:36 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc | 02/23/2026 19:29 |  | N |  |  |  |  | Tree fell and took down service drop at 107 Central St. Also needs electrician. ABB Order Id: 870716 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840901 | A
04/01/2026 11:33:53 | MECo | Bay State South | UXBRIDGE | ALDRICH ST | UXBRIDGE 321 | 05-321W2 | 15 | OH | 153 | 0 | 7.30 | 1116.35 | 02/23/2026 10:34 | 02/23/2026 18:15 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P71 Aldrich St. Trees fell, took down wires at P70 and P83 Aldrich. ABB Order Id: 871888 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810266 | A
04/01/2026 11:23:28 | MECo | Bay State South | DOUGLAS | OAK ST | WHITINS POND 320 | 05-320W5 | 5 |  | 7 | 0 | 7.72 | 54.02 | 02/23/2026 08:36 | 02/23/2026 16:19 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P23 Oak St, cause unknown. ABB Order Id: 871218 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810220 | A
04/01/2026 10:20:26 | MECo | Bay State South | QUINCY | BURGESS ST | FIELD STREET 1 | 07-1W8 | 15 | OH | 1 | 0 | 37.87 | 37.87 | 02/23/2026 09:42 | 02/24/2026 14:55 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses (2 of 3) P2 Burgess St. Cause: Unknown. ABB Order Id: 871524, 873997 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840877 | A
04/01/2026 10:17:51 | MECo | Bay State South | QUINCY | CHAPMAN ST | FIELD STREET 1 | 07-1W8 | 15 |  | 16 | 0 | 25.85 | 413.55 | 02/23/2026 08:49 | 02/24/2026 10:39 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 10:38 |  | N |  |  |  |  | Blown transformer fuse P13 Chapman St. Cause: Unknown. ABB Order Id: 871255 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840876 | A
04/01/2026 10:16:05 | MECo | Bay State South | HOLBROOK | PLYMOUTH ST | EAST HOLBROOK 2 | 07-2W1 | 5 | OH | 1 | 0 | 19.09 | 19.09 | 02/23/2026 18:57 | 02/24/2026 14:03 | Failed Equipment | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Failed service to 346 Plymouth St. ABB Order Id: 872856 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840862 | A
04/01/2026 10:13:34 | MECo | Bay State South | QUINCY | EUSTIS ST | FIELD STREET 1 | 07-1W8 | 5 | OH | 1 | 0 | 8.78 | 8.77 | 02/24/2026 18:32 | 02/25/2026 03:18 | Failed Equipment | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Replaced failed service to 18 Eustis St. ABB Order Id: 873954 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810897 | A
04/01/2026 10:06:36 | MECo | Bay State South | QUINCY | THAYER ST | FIELD STREET 1 | 07-1W6 | 5 | OH | 1 | 0 | 9.98 | 9.97 | 02/24/2026 10:55 | 02/24/2026 20:53 | Failed Equipment | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Replaced failed service to 11 Thayer St. ABB Order Id: 873541 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810829 | A
04/01/2026 09:46:07 | MECo | Bay State South | QUINCY | HANCOCK ST | FIELD STREET 1 | 07-1W6 | 15 | OH | 1 | 0 | 32.07 | 32.07 | 02/23/2026 18:36 | 02/25/2026 02:40 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses (2 of 3) P104 Hancock St. Cause: Unknown. ABB Order Id: 873196 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810887 | A
04/01/2026 09:42:47 | MECo | Bay State South | QUINCY | HANCOCK ST | FIELD STREET 1 | 07-1W6 | 15 | OH | 129 | 0 | 25.90 | 1470.66 | 02/23/2026 05:28 | 02/23/2026 20:00 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown B and C-phase line fuses (2 of 3) P131 Hancock St and P13 Adams St. Cause: Unknown. ABB Order Id: 870234, 872449 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810239 | A
04/01/2026 09:33:20 | MECo | Bay State South | DOUGLAS | WEST ST | WHITINS POND 320 | 05-320W4 | 15 | OH | 326 | 0 | 6.61 | 2155.77 | 02/23/2026 08:10 | 02/23/2026 16:32 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown 2 of 3 line fuses at P72 West St. Manually opened 3rd fuse Patrol found no cause. Blizzard 2026. ABB Order Id: 871119 ABB Order Id: 872544 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810225 | A
04/01/2026 09:27:35 | MECo | Bay State South | QUINCY | NEWPORT AVE | FIELD STREET 1 | 07-1W6 | 15 | OH | 437 | 0 | 68.88 | 6478.97 | 02/23/2026 07:21 | 02/23/2026 23:45 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/23/2026 23:44 |  | N |  |  |  |  | Blown line fuses P30 Newport Ave. Cause: Tree fell on primary P22 Newport Ave and took down service to 2 Oakland Ave. ABB Order Id: 872278, 870886, 872832, 870888, 874257 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840704 | A
04/01/2026 08:54:48 | MECo | Bay State South | WEYMOUTH | VINE ST | NORTH WEYMOUTH 6 | 07-6W1 | 5 | OH | 9 | 0 | 29.26 | 419.42 | 02/23/2026 10:14 | 02/24/2026 10:07 | Unknown | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown stepdown transformer fuse (1 of 3) P2 Vine St due to down primary. Manually opened remaining fuses to repair. ABB Order Id: 873215 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810477 | A
04/01/2026 08:48:21 | MECo | Bay State South | WEYMOUTH | SUMMIT ST | NORTH WEYMOUTH 6 | 07-6W1 | 15 |  | 11 | 0 | 31.41 | 345.40 | 02/23/2026 04:32 | 02/24/2026 11:57 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P8 Summit St. Cause: Unknown. ABB Order Id: 871952 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810533 | A
04/01/2026 08:44:54 | MECo | Bay State South | RANDOLPH | OAK ST | RANDOLPH 5 | 07-5W3 | 15 | OH | 37 | 0 | 24.85 | 918.83 | 02/23/2026 06:23 | 02/24/2026 07:13 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown C-phase line fuse (1 of 3) P26 Oak St. Cause: Broken tree limb took down primary P8 Pond Ln. ABB Order Id: 870431 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810431 | A
04/01/2026 08:41:42 | MECo | Bay State South | RANDOLPH | REILLY DR | RANDOLPH 5 | 07-5W3 | 15 |  | 6 | 0 | 30.59 | 183.50 | 02/23/2026 05:41 | 02/24/2026 12:17 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Burnt up transformer cutout tap P7 Reilley Dr. ABB Order Id: 872648 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810519 | A
04/01/2026 08:37:14 | MECo | Bay State South | QUINCY | NIGHTINGALE AVE | WEST QUINCY 3 | 07-3J3 | 5 | OH | 41 | 0 | 23.40 | 959.57 | 02/23/2026 07:26 | 02/24/2026 06:50 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses (2 of 3) P9 Nightingale Ave. Cause: Unknown. ABB Order Id: 870858 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810429 | A
04/01/2026 08:34:19 | MECo | Bay State South | WEYMOUTH | ALROY RD | EAST HOLBROOK 2 | 07-2W2 | 15 |  | 11 | 0 | 1.74 | 19.07 | 02/25/2026 12:18 | 02/25/2026 14:03 | Failed Equipment | Pole - wood |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Manually opened transformer fuse P4 Alroy Rd to replace leaning pole. ABB Order Id: 874307 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811049 | A
04/01/2026 08:19:50 | MECo | Bay State South | RANDOLPH | COLE TER | SOUTH RANDOLPH 97 | 07-97W3 | 15 | OH | 19 | 0 | 63.03 | 2867.75 | 02/23/2026 07:35 | 02/24/2026 20:06 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown C-phase line fuse (1 of 2) P13 Cole Ter. Cause: Tree fell and broke P2 Beverly Ter. Manually opened remaining fuse to make repairs. ABB Order Id: 870902, 871662 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810819 | A
04/01/2026 07:57:42 | MECo | Bay State South | HANOVER | MAIN ST | PHILLIPS LANE | 07-95W5 | 15 | OH | 352 | 0 | 2.03 | 709.87 | 02/23/2026 05:33 | 02/23/2026 07:34 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | Y | Tim Kane;Jason Cavallaro; | Email (Timothy.kane@hanover-ma.gov);Email (jason.cavallaro@hanover-ma.gov); |  |  | Pole top recloser P21 Main St locked out. Cause: Broken tree limb on primary P2-1 Main St. ABB Order Id: 870239 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810105 | A
04/01/2026 07:26:53 | MECo | Bay State South | HANOVER | SUMMER ST | PHILLIPS LANE | 07-95W4 | 5 | OH | 1 | 0 | 52.52 | 52.52 | 02/23/2026 08:21 | 02/25/2026 12:52 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken tree limb took down service to 84 Summer St - ran new service. ABB Order Id: 874195, 871152 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811027 | A
03/31/2026 14:09:03 | MECo | Bay State West | WORCESTER | BURNCOAT ST | GREENDALE 24 | 01-24W5 | 15 | OH | 19 | 0 | 0.69 | 12.98 | 02/23/2026 00:07 | 02/23/2026 00:49 | Failed Equipment | Tap |  | WIND | M | N | Y | N | tc | 02/23/2026 00:30 |  | N |  |  |  |  | Blown line fuse at P53 Burncoat St. Cause - burnt off high side transformer cutout tap at P3 Chatham Village Rd. ABB Order Id: 869906 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810084 | A
03/31/2026 09:18:18 | MECo | Bay State South | WEYMOUTH | WHITMAN ST | EAST WEYMOUTH 9 | 07-9W2 | 15 | OH | 2 | 0 | 6.09 | 12.17 | 02/24/2026 13:21 | 02/24/2026 19:27 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P7 Whitman St. Cause: Tree fell and took down primary P7-2 Whitman St. ABB Order Id: 873666 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810813 | A
03/31/2026 09:15:47 | MECo | Bay State South | WEYMOUTH | MIDDLE ST | EAST WEYMOUTH 9 | 07-9W2 | 5 | OH | 1 | 0 | 19.87 | 19.87 | 02/23/2026 17:07 | 02/24/2026 13:00 | Failed Equipment | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Replaced failed secondary connector to 141 Middle St. ABB Order Id: 872730 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810597 | A
03/31/2026 08:41:20 | MECo | Bay State South | SOUTHBOROUGH | NORTHBORO RD | NORTHBORO ROAD 317 | 05-317W3 | 15 | OH | 670 | 0 | 6.59 | 2467.92 | 02/23/2026 04:59 | 02/23/2026 11:36 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | 317W3 feeder locked out due to tree falling and taking 3 phases down at P37 Turnpike St, Southboro. Isolated with loadbreak at P87 and closed breaker. Blizzard 2026. ABB Order Id: 870107 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810141 | A
03/31/2026 07:31:30 | MECo | Bay State South | QUINCY | SAMOSET AVE | FIELD STREET 1 | 07-1W5 | 5 |  | 18 | 0 | 0.00 | 371.99 | 02/23/2026 05:50 | 02/24/2026 02:30 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 02:29 |  | N |  |  |  |  | Blown transformer fuse P13 Samoset Ave. Cause: Unknown. ABB Order Id: 872587 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840677 | A
03/31/2026 07:18:43 | MECo | Bay State South | QUINCY | SEA ST | FIELD STREET 1 | 07-1W5 | 15 | OH | 264 | 0 | 12.19 | 3134.78 | 02/23/2026 05:46 | 02/23/2026 17:58 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown A and B-phase line fuses (2 of 3) P57 Sea St. Cause: Broken tree limb on primary. ABB Order Id: 870285 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810265 | A
03/30/2026 15:47:36 | MECo | Bay State North | ROCKPORT | POOLE'S LN | ROCKPORT 40, RIVERDALE 52, ROCKPORT 40, ROCKPORT 40, ROCKPORT 40 | 12-2364, 12-40J1, 12-52L1, 12-40J4, 12-40J2, 12-40J3 | 15 |  | 5263 | 0 | 5.74 | 10273.30 | 02/23/2026 06:47 | 02/23/2026 10:38 | Failed Equipment | Tap |  | WIND | M | Y | Y | N | tc |  |  | N |  |  |  |  | 2364 Circuit Breaker locked out at Gloucester substation cause by failed lightning arrestor tap P1 Blackburn Circle. Riverdale 52L1 CB opened on 2364 UV relay as expected, with loop scheme operating restoring customers past P247 Washington St via 40L1 supply at P1296 Granite St. Closed P247 Washington restoring all 52L1 customers. Rockport 40 sub failed to transfer to it backup 2363 supply due to the 2363 Air Break not completing its open operation to the fully open position. This caused a loss of supply to all Rockport 4kV customers. Crews cleared failed LA, closed 2364 AB at Rockport de-energized, and restored all customers by closing 2364 CB at Gloucester. 40J1 customer count reduced due to previously existing outage 8810382 ABB Order Id: 870612 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810145 | A
03/30/2026 15:47:07 | MECo | Bay State North | ROCKPORT | TARRS LN | ROCKPORT 40 | 12-40J4 | 5 |  | 9 | 0 | 34.48 | 310.36 | 02/23/2026 15:45 | 02/25/2026 02:15 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken secondary neutral in crib from P102 Tarrs Ln caused by tree. Crew opened transformer fuse to repair. ABB Order Id: 872619 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810893 | A
03/30/2026 15:38:43 | MECo | Bay State South | PEMBROKE | JEAN ST | PHILLIPS LANE | 07-95W3 | 15 |  | 5 | 0 | 29.92 | 149.58 | 02/23/2026 12:18 | 02/24/2026 18:13 | Tree Contact | Transformer O/H conv. |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P2 Jean St. Cause: tree fell at P2 Jean St and damaged transformer and pulled secondary wires down. ABB Order Id: 872176 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810764 | A
03/30/2026 15:35:31 | MECo | Bay State South | HANSON | KING ST | PHILLIPS LANE | 07-95W3 | 15 | OH | 27 | 0 | 9.82 | 264.60 | 02/23/2026 12:06 | 02/23/2026 21:55 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P16 King St. No cause found on patrol. ABB Order Id: 872141 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810336 | A
03/30/2026 15:32:10 | MECo | Bay State South | HANSON | PINEHAVEN TRL | PHILLIPS LANE | 07-95W3 | 15 | OH | 5 | 0 | 29.28 | 146.33 | 02/23/2026 10:30 | 02/24/2026 15:47 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P31 Maquan St caused by tree branch on primary on Pinehaven Trail. ABB Order Id: 871863 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810641 | A
03/30/2026 15:28:43 | MECo | Bay State South | HANOVER | KING ST | PHILLIPS LANE | 07-95W3 | 15 | OH | 15 | 0 | 4.29 | 494.00 | 02/23/2026 09:28 | 02/24/2026 18:24 | Physical Interference / Company | No failure or Unknown |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P58 King St. Cause: tree contacted wire on King Hill Rd during high winds. ABB Order Id: 871446, 873709 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810766 | A
03/30/2026 15:21:13 | MECo | Bay State South | PEMBROKE | MONTCLAIR AVE | PHILLIPS LANE | 07-95W3 | 15 |  | 6 | 0 | 31.12 | 186.70 | 02/23/2026 09:07 | 02/24/2026 16:14 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P3 Montclair Ave. Cause: tree fell between P4 and P5 Montclair and broke secondary conductor. ABB Order Id: 871360 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810679 | A
03/30/2026 15:12:24 | MECo | Bay State South | HANSON | MAQUAN ST | PHILLIPS LANE | 07-95W3 | 15 | OH | 10 | 0 | 34.49 | 412.02 | 02/23/2026 06:45 | 02/24/2026 17:15 | Tree Contact | Overhead Device Other |  | WIND | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P10 Woodman Terrace. Cause: tree fell at P10 Woodman Terrace and hit transformer fuse and pulled wire off insulator. Manually opened line fuse P18 Maquan St to remove tree and pick phase up. ABB Order Id: 871673, 873664 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810705 | A
03/30/2026 14:31:18 | MECo | Bay State South | PEMBROKE | SCHOOL ST | PHILLIPS LANE | 07-95W3 | 15 | OH | 108 | 0 | 33.84 | 3655.05 | 02/23/2026 06:35 | 02/24/2026 16:25 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P61 School St (3 of 3). Cause: tree fell and broke crossarm at P70 School St and damaged 2 sections of conductor between P70-P72 School St. ABB Order Id: 871166 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810704 | A
03/30/2026 14:09:56 | MECo | Bay State South | PEMBROKE | CENTER ST | PHILLIPS LANE | 07-95W3 | 15 | OH | 149 | 0 | 40.43 | 6022.70 | 02/23/2026 05:59 | 02/24/2026 22:24 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P128 Center St (3 of 3). Cause: tree fell at P153 Center St and broke conductors and multiple crossarms. ABB Order Id: 871103, 870340 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810855 | A
03/30/2026 13:58:04 | MECo | Bay State South | NORTON | SOUTH WORCESTER ST | CHARTLEY POND 8 | 05-8L2 | 15 | OH | 73 | 0 | 11.71 | 837.45 | 02/23/2026 05:48 | 02/23/2026 17:33 | Tree Contact | No failure or Unknown |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse at P674 S Worcester St. Cause: tree down, location not specified. ABB Order Id: 870291 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810248 | A
03/30/2026 13:39:35 | MECo | Bay State South | NORTON | TODD DR | CHARTLEY POND 8 | 05-8L3 | 5 | OH | 1 | 0 | 24.93 | 24.92 | 02/23/2026 08:50 | 02/24/2026 09:45 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Rehung service drop damaged by falling tree at 9 Todd Dr. ABB Order Id: 871267 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810451 | A
03/30/2026 13:37:49 | MECo | Bay State South | NORTON | WALKER ST | CHARTLEY POND 8 | 05-8L3 | 15 | OH | 18 | 0 | 18.73 | 336.90 | 02/23/2026 05:34 | 02/24/2026 00:18 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse on P569 Walker St, cleared limb on Taylor St. ABB Order Id: 870243 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810366 | A
03/30/2026 12:45:54 | MECo | Bay State South | QUINCY | QUINCY AVE | FIELD STREET 1 | 07-1W4 | 15 | OH | 34 | 0 | 28.37 | 968.54 | 02/23/2026 07:29 | 02/24/2026 11:58 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown B and C-phase line fuses (2 of 3) P44 Quincy Ave. Cause: Unknown. ABB Order Id: 870880, 872742, 872941, 873472 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810508 | A
03/30/2026 11:58:51 | MECo | Bay State South | QUINCY | BLANCHARD RD | FIELD STREET 1 | 07-1W4 | 15 | OH | 49 | 0 | 20.68 | 1013.51 | 02/23/2026 05:23 | 02/24/2026 02:04 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses (2 of 3) P9 Blanchard Rd. Cause: Broken tree limb on primary on Faxon Ln. ABB Order Id: 870211 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810388 | A
03/30/2026 11:29:00 | MECo | Bay State South | QUINCY | QUINCY AVE | FIELD STREET 1 | 07-1W3 | 15 | OH | 82 | 0 | 12.17 | 996.30 | 02/23/2026 04:32 | 02/23/2026 16:42 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 16:20 |  | N |  |  |  |  | Blown B phase line fuse P65 Quincy Ave and blown B phase line fuse P2 West Howard St. No cause found on patrol. ABB Order ID: 870266, 870027 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8813658 | A
03/30/2026 11:28:50 | MECo | Bay State South | QUINCY | SOUTH ST | FIELD STREET 1 | 07-1W3 | 15 | OH | 607 | 0 | 10.64 | 6444.14 | 02/23/2026 05:38 | 02/23/2026 16:16 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 15:00 |  | N |  |  |  |  | Pole top recloser trip and reclose P23 Elm St and sectionalizing PTR P11 South St locked out on undervoltage. FLISR scheme operated and opened PTR P40 South St and closed PTR P54 Quincy Ave. No cause was found on patrol. ABB Order Id: 870252 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810222 | A
03/30/2026 11:23:08 | MECo | Bay State South | QUINCY | FIGUREHEAD LN | FIELD STREET 1 | 07-1W2 | 15 | OH | 1 | 0 | 23.51 | 23.50 | 02/23/2026 14:08 | 02/24/2026 13:39 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses (2 of 3) P54 Palmer St. Cause: Unknown. ABB Order Id: 873216 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810565 | A
03/30/2026 11:21:43 | MECo | Bay State South | QUINCY | HOOPER ST | FIELD STREET 1 | 07-1W2 | 5 |  | 11 | 0 | 22.22 | 244.40 | 02/23/2026 12:32 | 02/24/2026 10:45 | Failed Equipment | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Manually opened transformer fuse P6 Hooper St to replace burnt up secondaries. ABB Order Id: 872500 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810490 | A
03/30/2026 11:18:18 | MECo | Bay State South | QUINCY | JEWETT ST | FIELD STREET 1 | 07-1W2 | 15 |  | 8 | 0 | 28.60 | 228.67 | 02/23/2026 12:26 | 02/24/2026 17:02 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P2 Jewett St. Cause: Burnt up low-side transformer cutout tap. ABB Order Id: 872195 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810699 | A
03/30/2026 11:14:17 | MECo | Bay State South | QUINCY | SEA ST | FIELD STREET 1 | 07-1W2 | 15 | OH | 32 | 0 | 25.09 | 802.87 | 02/23/2026 09:14 | 02/24/2026 10:19 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P120 Sea St. Cause: Unknown. ABB Order Id: 871390, 872679 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810480 | A
03/30/2026 11:06:04 | MECo | Bay State South | WEYMOUTH | WASHINGTON ST | MID-WEYMOUTH 12 | 07-12W6 | 15 | OH | 51 | 0 | 25.65 | 1368.26 | 02/23/2026 11:10 | 02/24/2026 19:30 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P106 Washington St. Cause: Tree fell and took down primary P3 Island View Rd and the service to 986 Washington St apartments. ABB Order Id: 872005, 873703 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810539 | A
03/30/2026 10:53:26 | MECo | Bay State South | QUINCY | HILLSIDE AVE | NORTH QUINCY 11 | 07-11W4 | 5 | OH | 1 | 0 | 0.00 | 13.32 | 02/24/2026 12:38 | 02/25/2026 01:57 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 109 Hillside Ave. ABB Order Id: 873630 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840594 | A
03/30/2026 10:51:38 | MECo | Bay State South | WEYMOUTH | CENTRAL ST | MID-WEYMOUTH 12 | 07-12W5 | 15 | OH | 23 | 0 | 25.10 | 577.30 | 02/23/2026 09:04 | 02/24/2026 10:11 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P13 Central St. Cause: Unknown. ABB Order Id: 871350 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810475 | A
03/30/2026 10:47:54 | MECo | Bay State South | WEYMOUTH | MAIN ST | MID-WEYMOUTH 12 | 07-12W5 | 15 | OH | 57 | 0 | 14.83 | 845.14 | 02/23/2026 07:40 | 02/23/2026 22:30 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse (1 of 3) P129 Main St. Cause: Unknown. ABB Order Id: 871444 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810356 | A
03/30/2026 10:15:51 | MECo | Bay State South | WEYMOUTH | FRONT ST | MID-WEYMOUTH 12 | 07-12W5 | 15 | OH | 51 | 0 | 12.09 | 616.25 | 02/23/2026 05:04 | 02/23/2026 17:10 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P103 Front St. Cause: Unknown. ABB Order Id: 870122 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810247 | A
03/30/2026 10:07:39 | MECo | Bay State South | WEYMOUTH | UNION ST | MID-WEYMOUTH 12 | 07-12W4 | 15 |  | 3 | 0 | 25.67 | 76.95 | 02/23/2026 11:55 | 02/24/2026 13:35 | Tree Contact | Tap |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P86 Union St. Cause: Broken tree limb broke low-side transformer cutout tap. ABB Order Id: 872104 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810562 | A
03/30/2026 10:01:17 | MECo | Bay State South | QUINCY | MONTCLAIR AVE | NORTH QUINCY 11 | 07-11W4 | 5 | OH | 239 | 0 | 6.71 | 1363.10 | 02/23/2026 06:24 | 02/23/2026 12:06 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown stepdown transformer fuses P3, P4, and P5 Montclair Ave. Cause: Trees fell and took down primary along Vershire St, and broken tree limbs on primary along Sagamore Ave and Montclair Ave. ABB Order Id: 870537, 871950, 870841, 871029, 871945, 871954, 871971, 872028 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810172 | A
03/30/2026 09:56:11 | MECo | Bay State South | ATTLEBORO | NORTH AVE | READ STREET 9 | 05-9L1 | 15 | OH | 68 | 0 | 0.00 | 619.05 | 02/23/2026 10:05 | 02/23/2026 20:23 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/23/2026 20:22 |  | N |  |  |  |  | Blown line fuse P7977 North Ave - cause unknown. Blizzard. ABB Order Id: 871746 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840587 | A
03/30/2026 09:53:48 | MECo | Bay State South | ATTLEBORO | SEMPLE VILLAGE RD | READ STREET 9 | 05-9L1 | 5 | OH | 1 | 0 | 0.00 | 17.47 | 02/23/2026 09:29 | 02/24/2026 02:58 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc | 02/24/2026 02:56 |  | N |  |  |  |  | 122 Semple Village Rd, tree fell and took down service drop, customer also needs electrician. ABB Order Id: 871453 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840586 | A
03/30/2026 09:37:23 | MECo | Bay State South | QUINCY | HARVARD ST | NORTH QUINCY 11 | 07-11W4 | 15 | OH | 153 | 0 | 11.89 | 1763.03 | 02/23/2026 04:53 | 02/23/2026 16:25 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown A and B-phase line fuses (2 of 3) P31 Harvard St. Cause: Unknown. ABB Order Id: 870131, 870109 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810234 | A
03/30/2026 09:23:10 | MECo | Bay State South | ATTLEBORO | MIDDLE ST | READ STREET 9 | 05-9L1 | 5 |  | 1 | 0 | 27.94 | 36.23 | 02/23/2026 12:05 | 02/24/2026 16:02 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and broke pole 8362 Middle St. Pole replaced transformer transferred. ABB Order Id: 872133 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810646 | A
03/30/2026 09:10:11 | MECo | Bay State South | ATTLEBORO | SOUTH AVE | READ STREET 9 | 05-9L1 | 15 | OH | 77 | 0 | 5.27 | 277.84 | 02/23/2026 07:45 | 02/23/2026 11:21 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P6984 at corner of Burt and South St. Cause: tree fell at P9037 Odonnell Dr. ABB Order Id: 871002 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810162 | A
03/30/2026 09:04:44 | MECo | Bay State South | QUINCY | FARRINGTON ST | NORTH QUINCY 11 | 07-11W2 | 5 | OH | 1 | 0 | 30.68 | 30.68 | 02/23/2026 18:41 | 02/25/2026 01:22 | Failed Equipment | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Failed service to 227 Farrington St - ran new service. ABB Order Id: 872837 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810879 | A
03/30/2026 08:49:51 | MECo | Bay State South | SCITUATE | OLD OAKEN BUCKET RD | SCITUATE SUB | 07-915W35 | 15 | OH | 8 | 0 | 40.06 | 320.51 | 02/23/2026 12:50 | 02/25/2026 04:54 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P51 Old Oaken Bucket Rd. Cause: Tree fell and broke P4 Marilyn Rd. ABB Order Id: 874081 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810916 | A
03/30/2026 08:48:58 | MECo | Bay State South | ATTLEBORO | HANISCH RD | READ STREET 9 | 05-9L1 | 15 | OH | 13 | 0 | 29.68 | 385.88 | 02/23/2026 06:56 | 02/24/2026 12:38 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P9182 Hanisch Rd. Cause - tree fell at P9059 Hillcrest, with broken pole. Repaired primary and secondary from P9183 Hanisch Rd to P9059 Hillcrest Rd. ABB Order Id: 870713 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810547 | A
03/30/2026 08:47:16 | MECo | Bay State South | NORWELL | CROSS ST | SCITUATE SUB | 07-915W35 | 15 | OH | 2 | 0 | 27.77 | 55.53 | 02/23/2026 12:27 | 02/24/2026 16:13 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P6-1 Cross St. Cause: Tree fell and broke primary P6-11 Cross St. ABB Order Id: 872198 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810656 | A
03/30/2026 08:43:50 | MECo | Bay State South | NORWELL | MAIN ST | SCITUATE SUB | 07-915W35 | 15 | OH | 61 | 0 | 30.19 | 1841.18 | 02/23/2026 11:50 | 02/24/2026 18:02 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P424 Main St. Cause: Tree fell and took down primary P16 Neal Gate St. ABB Order Id: 872099 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810749 | A
03/30/2026 08:39:50 | MECo | Bay State South | SCITUATE | FIRST PARISH RD | SCITUATE SUB | 07-915W35 | 15 |  | 5 | 0 | 33.80 | 168.92 | 02/23/2026 11:13 | 02/24/2026 21:01 | Failed Equipment | Cutout - open |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P173 First Parish Rd. Cause: Failed cutout. ABB Order Id: 873055 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810832 | A
03/30/2026 08:39:46 | MECo | Bay State South | ATTLEBORO | TIFFANY ST | READ STREET 9 | 05-9L2 | 15 | OH | 141 | 0 | 11.83 | 1522.41 | 02/23/2026 06:06 | 02/23/2026 17:57 | Tree Contact | Transformer O/H conv. |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse 100k at P4676 Tiffany St Attleboro, at P4685 Tiffany St, tree feel on transformer and cutout, replaced 25kVA transformer. ABB Order Id: 870387 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810253 | A
03/30/2026 08:36:51 | MECo | Bay State South | SCITUATE | FIRST PARISH RD | SCITUATE SUB | 07-915W35 | 5 | OH | 43 | 0 | 40.44 | 1738.63 | 02/23/2026 08:16 | 02/25/2026 00:42 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown stepdown transformer fuse P162 First Parish Rd. Cause: Broken tree limb took down primary between P5 and P6 Vernon Rd. ABB Order Id: 871136 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810873 | A
03/30/2026 08:36:19 | MECo | Bay State South | ATTLEBORO | LOCUST ST | READ STREET 9 | 05-9L4 | 15 | OH | 17 | 0 | 29.92 | 508.58 | 02/23/2026 11:00 | 02/24/2026 16:56 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P4710 Locust St. Cause - tree fell at P8755 Bayberry Hill Rd. Primary between P8755 and P8756 off pin and replaced pole at P8755. ABB Order Id: 871981 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810698 | A
03/30/2026 08:31:22 | MECo | Bay State South | SCITUATE | MAPLE ST | SCITUATE SUB | 07-915W35 | 15 | OH | 60 | 0 | 30.36 | 1821.80 | 02/23/2026 08:03 | 02/24/2026 14:25 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P35 Maple St. Cause: Tree fell on primary P51 Winter St. ABB Order Id: 873323, 871066, 871898 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810629 | A
03/30/2026 08:26:38 | MECo | Bay State South | NORWELL | CROSS ST | SCITUATE SUB | 07-915W35 | 5 | OH | 2 | 0 | 0.00 | 69.75 | 02/23/2026 07:04 | 02/24/2026 17:57 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down services to 111 and 112 Cross St. ABB Order Id: 870751 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840577 | A
03/30/2026 08:24:08 | MECo | Bay State South | SCITUATE | CORNET STETSON RD | SCITUATE SUB | 07-915W35 | 15 | OH | 11 | 0 | 0.00 | 500.15 | 02/23/2026 06:41 | 02/25/2026 04:10 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 19:58 |  | N |  |  |  |  | Blown B-phase line fuse (1 of 3) P431 Cornet Stetson Rd. Cause: Unknown. ABB Order Id: 870574 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840576 | A
03/30/2026 07:40:30 | MECo | Bay State South | PEMBROKE | PELHAM ST | WATER STREET #910 | 07-910W25 | 15 | OH | 44 | 0 | 40.10 | 1780.27 | 02/23/2026 07:17 | 02/24/2026 23:23 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown A-phase line fuse (1 of 3) P6 Pelham St and blown line fuse P5 Station St. Cause: Tree fell and broke P5 and P5-30 Station St. ABB Order Id: 871633, 874032 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810856 | A
03/30/2026 07:35:01 | MECo | Bay State South | PEMBROKE | HOBOMOCK ST | WATER STREET #910 | 07-910W25 | 5 | OH | 1 | 0 | 0.00 | 19.73 | 02/23/2026 22:45 | 02/24/2026 00:57 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 151 Hobomock St. ABB Order Id: 873062, 873291 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840572 | A
03/30/2026 07:31:24 | MECo | Bay State South | PEMBROKE | LITTLES AVE | WATER STREET #910 | 07-910W25 | 5 | OH | 2 | 0 | 1.78 | 30.55 | 02/24/2026 16:45 | 02/25/2026 08:02 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down services to 44 and 46 Littles Ave. ABB Order Id: 873814, 873978 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810770 | A
03/30/2026 07:24:41 | MECo | Bay State South | PEMBROKE | OLD PELHAM ST | WATER STREET #910 | 07-910W25 | 5 | OH | 1 | 0 | 0.00 | 8.64 | 02/24/2026 09:55 | 02/24/2026 18:34 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 18:34 |  | N |  |  |  |  | Tree fell and took down service to 141 Old Pelman St. ABB Order Id: 873492 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840570 | A
03/30/2026 07:20:30 | MECo | Bay State South | PEMBROKE | FOREST ST | WATER STREET #910 | 07-910W25 | 5 | OH | 1 | 0 | 0.00 | 50.99 | 02/23/2026 14:18 | 02/24/2026 01:13 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 315 Forest St. ABB Order Id: 872472, 874377, 873425 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840569 | A
03/30/2026 07:16:39 | MECo | Bay State South | PEMBROKE | FURNACE LN | WATER STREET #910 | 07-910W25 | 15 | OH | 16 | 0 | 0.00 | 103.10 | 02/23/2026 10:27 | 02/24/2026 16:54 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 16:01 |  | N |  |  |  |  | Blown line fuse P11 Furnace Ln. Cause: Tree fell and took down primary P20 Furnace Ln. ABB Order Id: 871845 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840568 | A
03/30/2026 07:01:34 | MECo | Bay State South | PEMBROKE | BIRCH ST | WATER STREET #910 | 07-910W25 | 5 | OH | 1 | 0 | 0.36 | 24.36 | 02/23/2026 14:15 | 02/24/2026 14:37 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken tree limb took down service to 58 Birch St - electrician needed. ABB Order Id: 873716 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810605 | A
03/30/2026 06:55:23 | MECo | Bay State South | PEMBROKE | W ELM ST | WATER STREET #910 | 07-910W25 | 15 | OH | 1 | 0 | 51.86 | 51.85 | 02/23/2026 12:22 | 02/25/2026 16:13 | Tree Contact | Overhead Device Other |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P25 W Elm St. Cause: Tree fell and knocked phase off pins at multiple locations between P25 and P25-38 W Elm St. ABB Order Id: 873208 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811072 | A
03/30/2026 06:51:54 | MECo | Bay State South | PEMBROKE | LITTLES AVE | WATER STREET #910 | 07-910W25 | 15 | OH | 34 | 0 | 28.88 | 982.03 | 02/23/2026 11:24 | 02/24/2026 16:17 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P6 Littles Ave. Cause: Broken tree limb on primary P10 Littles Ave. ABB Order Id: 872052 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810670 | A
03/30/2026 06:48:59 | MECo | Bay State South | PEMBROKE | W ELM ST | WATER STREET #910 | 07-910W25 | 15 | OH | 90 | 0 | 31.26 | 2696.53 | 02/23/2026 09:58 | 02/24/2026 17:17 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | TripSaver found open P39 W Elm St. Cause: Tree fell and took down primary P27 Dwelley St. ABB Order Id: 872769 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810727 | A
03/30/2026 06:34:41 | MECo | Bay State South | PEMBROKE | VALLEY ST | WATER STREET #910 | 07-910W25 | 15 | OH | 45 | 0 | 30.35 | 1365.00 | 02/23/2026 10:00 | 02/24/2026 16:21 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | TripSaver found open P28 Valley St. Cause: Tree fell and took down primary P42 Valley St. ABB Order Id: 872852 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810672 | A
03/30/2026 06:26:44 | MECo | Bay State South | PEMBROKE | OLDHAM ST | WATER STREET #910 | 07-910W25 | 5 | OH | 1 | 0 | 34.03 | 34.03 | 02/23/2026 09:08 | 02/24/2026 19:11 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken tree limb took down service to 151 Oldham St - reattached service. ABB Order Id: 871369 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810793 | A
03/30/2026 06:24:57 | MECo | Bay State South | PEMBROKE | MONROE ST | WATER STREET #910 | 07-910W25 | 5 | OH | 1 | 0 | 0.00 | 51.28 | 02/23/2026 06:57 | 02/24/2026 17:01 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken tree limb took down service to 105 Monroe St. ABB Order Id: 870717, 873830 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840567 | A
03/30/2026 06:16:25 | MECo | Bay State South | PEMBROKE | CHESTNUT RD | WATER STREET #910 | 07-910W25 | 15 | OH | 27 | 0 | 32.58 | 879.30 | 02/23/2026 06:19 | 02/24/2026 14:54 | Tree Contact | Overhead Device Other |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P2 Chestnut Rd. Cause: Broken tree limb knocked phase off pin P5 Chestnut Rd. ABB Order Id: 870440 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810606 | A
03/30/2026 06:13:51 | MECo | Bay State South | PEMBROKE | CHAPEL ST | WATER STREET #910 | 07-910W25 | 15 | OH | 35 | 0 | 34.62 | 426.65 | 02/23/2026 05:48 | 02/24/2026 16:26 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P25 Chapel St. Cause: Tree fell and took down primary P2 Yale Rd. ABB Order Id: 870284 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810677 | A
03/29/2026 11:12:12 | MECo | Bay State South | QUINCY | EAST SQUANTUM ST | NORTH QUINCY 11 | 07-11W1 | 15 | OH | 3 | 0 | 4.48 | 13.43 | 02/24/2026 13:42 | 02/24/2026 18:11 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown B and C-phase line fuse (2 of 3) P63 East Squantum St. Cause: Unknown. ABB Order Id: 873685 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810756 | A
03/29/2026 10:56:29 | MECo | Bay State South | COHASSET | KING ST | KING STREET UNIT 18 | 07-18J1 | 5 | OH | 19 | 0 | 3.42 | 879.68 | 02/23/2026 05:58 | 02/25/2026 04:15 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown B-phase line fuse (1 of 3) P44 King St. Cause: Broken tree limb on Chief Justice Cushing Hwy. ABB Order Id: 874040, 870322 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810914 | A
03/29/2026 10:16:54 | MECo | Bay State South | SCITUATE | ELM ST | SCITUATE SUB | 07-915W82 | 15 | OH | 11 | 0 | 5.86 | 95.28 | 02/24/2026 18:20 | 02/25/2026 00:11 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P26 Elm St. Cause: Unknown. ABB Order Id: 873948, 874035 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810867 | A
03/29/2026 10:13:02 | MECo | Bay State South | SCITUATE | THOMAS AVE | SCITUATE SUB | 07-915W82 | 5 | OH | 1 | 0 | 29.64 | 29.63 | 02/23/2026 10:31 | 02/24/2026 16:10 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken tree limb took down service to 38 Thomas Ave - reattached service. ABB Order Id: 871867 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810667 | A
03/29/2026 08:52:08 | MECo | Bay State South | ATTLEBORO | VENUS WAY | READ STREET 9 | 05-9L5 | 15 | OH | 1345 | 0 | 4.96 | 6074.34 | 02/23/2026 05:40 | 02/24/2026 18:10 | Tree Contact | Anchor and Guy |  | BLIZ | M | Y | Y | N | tc |  |  | Y | Mark Haskell;Deborah Arruda; | Email (mhaskell@rehobothfire.com);Email (darruda@rehobothma.gov); |  |  | Pole top recloser lockout at P11-1 R/W off Venus Dr. Tree fell and broke guy wire at P3718 Pine St. Blizzard 2026. Repaired secondary, replace an anchor and refuse P3718. ABB Order Id: 871907 ABB Order Id: 870258 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810128 | A
03/29/2026 08:32:19 | MECo | Bay State South | SCITUATE | FIRST PARISH RD | SCITUATE SUB | 07-915W82 | 15 | OH | 176 | 0 | 12.60 | 5341.01 | 02/23/2026 08:46 | 02/24/2026 17:36 | Tree Contact | Overhead Device Other |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P71 First Parish Rd. Cause: Broken tree limb knocked phases off pins along First Parish Rd. ABB Order Id: 873469, 871535, 873470 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810752 | A
03/29/2026 07:31:52 | MECo | Bay State South | SCITUATE | BRANCH ST | SCITUATE SUB | 07-915W82 | 15 | OH | 126 | 0 | 0.00 | 5797.02 | 02/23/2026 07:21 | 02/25/2026 05:21 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P40 Branch St. Cause: Tree fell and took down primary along Branch St and knocked phases off pins. ABB Order Id: 871059, 871291, 873801, 873319 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810449 | A
03/29/2026 07:08:35 | MECo | Bay State South | SCITUATE | TILDEN RD | SCITUATE SUB | 07-915W82 | 15 | OH | 29 | 0 | 4.32 | 1409.40 | 02/23/2026 04:14 | 02/25/2026 04:50 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown riser fuse P98 Tilden Rd. Cause: Broken tree limb. ABB Order Id: 869980, 874038, 873466 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810941 | A
03/29/2026 06:57:36 | MECo | Bay State South | SCITUATE | FIRST PARISH RD | SCITUATE SUB | 07-915W82 | 15 | OH | 420 | 0 | 20.63 | 6917.63 | 02/23/2026 12:56 | 02/24/2026 05:24 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | 915W82 circuit breaker at Scituate sub locked out. Cause: Tree fell and took down primary P3 Beaver Dam Rd and P40 Tilden Rd. Customer counts reduced due to prior side tap outages and concurrent outages beyond pole top reclosers P86 and P33 Tilden Rd. ABB Order Id: 872308 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810442 | A
03/29/2026 06:11:54 | MECo | Bay State South | SCITUATE | TILDEN RD | SCITUATE SUB | 07-915W82 | 15 | OH | 415 | 0 | 29.28 | 12151.55 | 02/23/2026 04:46 | 02/24/2026 10:03 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser P86 Tilden Rd locked out. Cause: Tree fell and took down primary P42 Tilden Rd. Customer count reduced due to concurrent outage beyond PTR P33 Tilden Rd. ABB Order Id: 870050 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810715 | A
03/28/2026 11:02:45 | MECo | Bay State South | ATTLEBORO | WEST ST | WEST STREET 1 | 05-1J2 | 5 | OH | 80 | 0 | 2.80 | 223.56 | 02/24/2026 13:27 | 02/24/2026 16:15 | Tree Contact | Crossarm |  | NORM | M | N | Y | N | tc |  |  | N |  |  |  |  | Manually opened 4-2 breaker at West St Sub to de-energize 1J2 feeder (1J2 being carried by 4-2 CB) to make repairs to broken crossarm P8447 N. Main St R/W due to fallen tree. ABB Order Id: 873670 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810676 | A
03/28/2026 10:50:25 | MECo | Bay State South | SCITUATE | TILDEN RD | SCITUATE SUB | 07-915W82 | 15 | OH | 1692 | 0 | 49.72 | 69771.06 | 02/23/2026 04:20 | 02/25/2026 11:05 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser P33 Tilden Rd locked out. Cause: Tree fell and damaged Hendrix P22 Hollet St and pulled primary out of dead-end shoe P16 Hollet St. Opened load break P32 Gannett Rd to isolate and restored some customers on a feeder tie. Opened line fuses P61 Gannett Rd due to further damage on Gannett Rd and closed PTR P33 Tilden Rd once mainline repairs complete. Multiple side taps remained out following restoration of mainline. ABB Order Id: 870006, 874118, 874063, 874093, 869977 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810936 | A
03/28/2026 10:32:50 | MECo | Bay State South | ATTLEBORO | WEST ST | WEST STREET 1 | 05-1J2 | 5 | OH | 80 | 0 | 5.16 | 393.87 | 02/23/2026 09:12 | 02/23/2026 14:27 | Tree Contact | Crossarm |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | 8420 breaker (69kV) trip and reclose at Read St Sub. 2TR lockout at West St Sub. Pole top recloser trip and reclose at P389 County St on 24 line. 1J2 breaker tripped due to a fallen tree/broken crossarm P8447 R/W on out the feeder, and one of the 4kV reactors between 2TR tertiary and the 4kV bus failed. 1J1 transferred OK to 1TR, but since 1J2 breaker was open on fault, 4-2 tie breaker did not close (proper). Note: most of 1J2 feeder is backfed for some mainline U/G cable replacement ongoing, so customer count is reduced. ABB Order Id: 872362 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810194 | A
03/28/2026 08:38:18 | MECo | Bay State South | DIGHTON | CENTER ST | DIGHTON | 05-19W74 | 15 | OH | 1 | 0 | 18.88 | 18.88 | 02/23/2026 13:57 | 02/24/2026 08:50 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P109 Center St. Broken tree on wires, broken primary. Resleeved and refused 6K at P109. ABB Order Id: 873213 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810598 | A
03/28/2026 08:34:11 | MECo | Bay State South | DIGHTON | WALKER ST | DIGHTON | 05-19W74 | 15 | OH | 1 | 0 | 35.82 | 35.82 | 02/23/2026 08:18 | 02/24/2026 20:08 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P10 Walker St. Tree took down wires and poles. Replaced poles and transformer P10-35 to restore. ABB Order Id: 871140 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811124 | A
03/28/2026 08:26:33 | MECo | Bay State South | DIGHTON | HORTON ST | DIGHTON | 05-19W73 | 15 | OH | 88 | 0 | 16.93 | 1488.67 | 02/23/2026 08:49 | 02/24/2026 01:45 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P64 Horton St cause was tree took down primary P49 - P51 Horton St. Blizzard 2026. ABB Order Id: 871261 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810389 | A
03/28/2026 08:20:17 | MECo | Bay State South | SWANSEA | GARDNER NECK RD | SWANSEA 11 | 05-11W84 | 5 | OH | 1 | 0 | 0.88 | 22.58 | 02/23/2026 16:10 | 02/24/2026 14:45 | Failed Equipment | Connector |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | House 439, P43 Gardners Neck Rd. Service pulled off house. Re attached service mid span between P43 and 44. ABB Order Id: 873698 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810639 | A
03/28/2026 08:16:36 | MECo | Bay State South | SWANSEA | LOCUST ST | SWANSEA 11 | 05-11W84 | 15 | OH | 53 | 0 | 0.61 | 31.80 | 02/24/2026 09:38 | 02/24/2026 10:15 | Tree Contact | No failure or Unknown |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Manually opened line fuses P45 Locust St. Found tree limb on wires P17, had to de-energize to safely remove. ABB Order Id: 873467 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810478 | A
03/28/2026 08:11:33 | MECo | Bay State South | SWANSEA | STEVENS RD | SWANSEA 11 | 05-11W84 | 15 | OH | 1 | 0 | 29.35 | 29.35 | 02/23/2026 09:10 | 02/24/2026 14:31 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P54 Stevens Rd. Not accessible - needed plow & tree crew. Primary down. ABB Order Id: 871379 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810595 | A
03/28/2026 07:56:46 | MECo | Bay State South | FALL RIVER | INDIANTOWN RD | BATES 115 | 05-115W52 | 15 | OH | 47 | 0 | 2.47 | 115.93 | 02/25/2026 01:06 | 02/25/2026 03:35 | Tree Contact | No failure or Unknown |  | NORM | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P61 Indiantown Rd due to fallen tree between P62 and 63 Indiantown. ABB Order Id: 874058 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810901 | A
03/28/2026 07:48:10 | MECo | Bay State South | FALL RIVER | INDIANTOWN RD | BATES 115 | 05-115W52 | 15 | OH | 30 | 0 | 24.66 | 1049.91 | 02/23/2026 10:13 | 02/25/2026 03:35 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse (1 of 3) P3 Indiantown Rd and blown line fuse (1 of 3) P32 Yellowhill Rd - cause unknown. Heavy snowstorm. Roads not plowed, had to wait on the town of Fall River to plow road. ABB Order Id: 873543 ABB Order Id: 873546, 873942 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810543 | A
03/28/2026 07:02:34 | MECo | Bay State South | WESTPORT | STATE RD | BATES 115 | 05-115W52 | 15 |  | 6 | 0 | 1.54 | 9.20 | 02/23/2026 05:30 | 02/23/2026 07:03 | Failed Equipment | Tap |  | WIND | M | N | Y | N | tc | 02/23/2026 06:10 |  | N |  |  |  |  | Failed tap wire to transformer at P18 State Rd. ABB Order Id: 870232 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810107 | A
03/27/2026 14:37:37 | NanECo | Bay State South | NANTUCKET | MILESTONE LN | CANDLE STREET 101 | 04-101L8 | 15 | OH | 23 | 0 | 16.81 | 386.40 | 02/24/2026 09:37 | 02/25/2026 02:25 | Failed Equipment | Overhead Device Other |  | SNOW | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P3 Milestone Rd. Broken poletop pin caused crossarm to burn at P3 Milestone Ln. Replaced pin, crossarm, and cutout. ABB Order Id: 873462 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810888 | A
03/27/2026 14:18:57 | NanECo | Bay State South | NANTUCKET | SPARKS AVE | CANDLE STREET 101 | 04-101L8 | 15 | OH | 3 | 0 | 70.97 | 212.90 | 02/23/2026 20:17 | 02/26/2026 19:15 | Physical Interference / Company | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Down primaries sagging from ice caused line fuse at P4 Sparks Ave to open. Refused with 40k fuse. Blizzard 2026. ABB Order Id: 873273 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811221 | A
03/27/2026 14:13:28 | NanECo | Bay State South | NANTUCKET | HOOPER FARM RD | CANDLE STREET 101 | 04-101L8 | 15 | OH | 82 | 0 | 0.00 | 3970.98 | 02/23/2026 13:48 | 02/26/2026 13:08 | Failed Equipment | Splice |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse (1 of 3) at P0-50 Hooper Farm Rd due to multiple wires down caused by ice accumulation resulting in failed splices. Customers restored at 1100. ABB Order Id: 872428 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840452 | A
03/27/2026 13:52:09 | MECo | Bay State South | HANOVER | FIRST ST | PHILLIPS LANE | 07-95W2 | 15 | OH | 1 | 0 | 25.43 | 25.42 | 02/24/2026 13:29 | 02/25/2026 14:55 | Tree Contact | Conductors |  | NORM | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P10 First St (3 of 3). Cause: tree fell and broke conductor in R/W off P10 First St. Lack of access because area was not plowed delayed restoration. ABB Order Id: 873671 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811058 | A
03/27/2026 13:03:24 | NanECo | Bay State South | NANTUCKET | PLEASANT ST | CANDLE STREET 101 | 04-101L8 | 15 |  | 17 | 0 | 67.67 | 1150.33 | 02/23/2026 13:14 | 02/26/2026 08:54 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P23 Pleasant St. Branch on bushing. Blizzard 2026 ABB Order Id: 873004 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811162 | A
03/27/2026 13:01:31 | NanECo | Bay State South | NANTUCKET | MILESTONE RD | CANDLE STREET 101 | 04-101L8 | 15 | OH | 1038 | 0 | 0.95 | 23399.91 | 02/23/2026 07:52 | 02/25/2026 21:33 | Failed Equipment | Pole - wood |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Phases had come down at P1 Tom Nevers Rd (see other IDS event for these 571 customers). Manually opened loadbreak P112 Milestone Rd. Tried to re-energize after lifting taps to Tom Nevers Rd, closed at P112, upstream PTR locked out (see other IDS event for P92 PTR lockout), and downstream PTR at P152 Milestone locked out with two dead phases. Isolated at P152 Milestone Rd and backfed most customers from 101L2. Blizzard 2026. Damage was becoming severe at this point, so area was left de-energized, and repairs made when the storm abated. ABB Order Id: 870910 Phases down P143-144 Milestone. Phases down at P148-149 Milestone Rd. Taps were lifted at P136 Milestone Rd, so about 70 customers could be restored. Area was de-energized briefly on 2/28 to put the taps back on and switch the feeder to normal configuration (see other IDS event). ABB Order Id: 871492 ABB Order Id: 872170, 870910 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811192 | A
03/27/2026 12:13:39 | MECo | Bay State South | HANOVER | CROSS ST | PHILLIPS LANE | 07-95W2 | 15 | OH | 148 | 0 | 29.45 | 5188.24 | 02/23/2026 08:22 | 02/24/2026 13:43 | Tree Contact | Pole - wood |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P2 Cross St, Hanover (1 of 3) and blown line fuse P2 State St, Hanson. Cause: tree fell and broke P2 State St. Manually opened remaining 2 fuses at P2 Cross St to make repairs. ABB Order Id: 871164 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810787 | A
03/27/2026 11:15:25 | MECo | Bay State South | SCITUATE | KENT ST | SCITUATE SUB | 07-915W36 | 15 | OH | 12 | 0 | 2.40 | 65.59 | 02/25/2026 10:33 | 02/25/2026 12:58 | Tree Contact | Lightning arrester |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse (1 of 3) P10 Kent St. Cause: Tree limb fell and broke arrestor. ABB Order Id: 874213, 874362 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811040 | A
03/27/2026 11:02:38 | MECo | Bay State South | SCITUATE | TURNER RD | SCITUATE SUB | 07-915W36 | 5 | OH | 1 | 0 | 10.30 | 10.28 | 02/25/2026 04:04 | 02/25/2026 14:22 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken tree limb took down service to 188 Tilden Rd - reattached service. ABB Order Id: 874072 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811054 | A
03/27/2026 10:57:18 | MECo | Bay State South | SCITUATE | CHIEF JUSTICE CUSHING HWY | SCITUATE SUB | 07-915W36 | 15 | OH | 1 | 0 | 0.00 | 22.59 | 02/24/2026 12:50 | 02/25/2026 11:26 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc | 02/25/2026 11:25 |  | N |  |  |  |  | Failed low-side tap to cutout P76 Chief Justice Cushing Hwy. ABB Order Id: 874061 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840351 | A
03/27/2026 10:55:51 | MECo | Bay State South | PEMBROKE | MATTAKEESETT ST | PHILLIPS LANE | 07-95W2 | 15 | OH | 71 | 0 | 32.98 | 2252.44 | 02/23/2026 08:35 | 02/24/2026 16:18 | Tree Contact | Conductors |  | WIND | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses (3 of 3) P46 Mattakeesett St. Cause: tree fell P5 Phillips St and caused wires down, broke multiple crossarms and damaged transformer. ABB Order ID: 870827, 871229 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810719 | A
03/27/2026 10:54:47 | MECo | Bay State South | SCITUATE | CHIEF JUSTICE CUSHING HWY | SCITUATE SUB | 07-915W36 | 5 | OH | 1 | 0 | 28.47 | 28.47 | 02/24/2026 08:47 | 02/25/2026 13:15 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 361 Chief Justice Cushing Hwy - ran new service. ABB Order Id: 873414 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811030 | A
03/27/2026 10:53:18 | MECo | Bay State South | SCITUATE | GREENFIELD LN | SCITUATE SUB | 07-915W36 | 5 | OH | 1 | 0 | 37.19 | 37.18 | 02/23/2026 19:03 | 02/25/2026 08:15 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Broken tree limb took down service to 11 Bunny Ln - reattached service. ABB Order Id: 872861 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810963 | A
03/27/2026 10:51:34 | MECo | Bay State South | SCITUATE | GREENFIELD LN | SCITUATE SUB | 07-915W36 | 5 |  | 1 | 0 | 34.56 | 34.56 | 02/23/2026 13:23 | 02/24/2026 23:57 | Failed Equipment | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Service pulled from house during high winds to 22 Greenfield Ln. Manually opened transformer fuse P20 Greenfield Ln to make repairs. ABB Order Id: 873809 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810865 | A
03/27/2026 10:41:36 | MECo | Bay State South | SCITUATE | STOCKBRIDGE RD | SCITUATE SUB | 07-915W36 | 15 | OH | 20 | 0 | 36.95 | 739.00 | 02/23/2026 12:42 | 02/25/2026 01:40 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P46 Stockbridge Rd. Cause: Unknown. ABB Order Id: 873039 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810883 | A
03/27/2026 10:40:17 | MECo | Bay State South | SCITUATE | CEDAR CREST LN | SCITUATE SUB | 07-915W36 | 5 |  | 7 | 0 | 46.20 | 323.40 | 02/23/2026 07:26 | 02/25/2026 05:39 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P4 Cedar Crest Ln due to broken tree limbs. ABB Order Id: 870864 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810942 | A
03/27/2026 10:17:19 | MECo | Bay State South | SCITUATE | CHIEF JUSTICE CUSHING HWY | SCITUATE SUB | 07-915W36 | 15 | OH | 57 | 0 | 5.27 | 2222.11 | 02/23/2026 07:00 | 02/24/2026 22:00 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P61 Chief Justice Cushing Hwy. Cause: Tree fell and took down primary P15 Satuit Trl. ABB Order Id: 873836, 870750 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810841 | A
03/27/2026 10:02:47 | MECo | Bay State South | SCITUATE | CHIEF JUSTICE CUSHING HWY | SCITUATE SUB | 07-915W36 | 15 | OH | 18 | 0 | 0.00 | 79.50 | 02/25/2026 07:06 | 02/25/2026 11:31 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown B-phase riser fuse (1 of 3) P22 Chief Justice Cushing Hwy. Cause: Unknown. ABB Order Id: 874188 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840366 | A
03/27/2026 09:50:09 | MECo | Bay State South | SCITUATE | COUNTRY WAY | SCITUATE SUB | 07-915W36 | 15 | OH | 74 | 0 | 31.88 | 2361.09 | 02/23/2026 10:06 | 02/24/2026 18:01 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown B and C-phase line fuses (2 of 3) P460 Chief Justice Cushing Hwy. Cause: Unknown. ABB Order Id: 871813, 873292 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810741 | A
03/27/2026 08:47:55 | MECo | Bay State South | SCITUATE | CRESCENT AVE | SCITUATE SUB | 07-915W36 | 15 |  | 8 | 0 | 10.86 | 86.85 | 02/24/2026 23:16 | 02/25/2026 10:08 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Failed transformer tap P1 Crescent Ave. ABB Order Id: 874029 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810993 | A
03/27/2026 08:46:27 | NanECo | Bay State South | NANTUCKET | MILESTONE RD | CANDLE STREET 101 | 04-101L8 | 15 | OH | 444 | 0 | 0.00 | 452.02 | 02/23/2026 08:34 | 02/23/2026 09:35 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser lockout at P92 Milestone Rd when closing loadbreak P112 Milestone Rd (see other IDS event) after making temporary repairs at Tom Nevers Rd. Blizzard 2026, ice covered wires blowing together in the wind. Isolated at P112 Milestone again and closed PTR. ABB Order ID: 871214 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840359 | A
03/27/2026 08:08:09 | MECo | Bay State South | SCITUATE | DRIFTWAY ST | SCITUATE SUB | 07-915W36 | 15 | OH | 220 | 0 | 46.06 | 9139.57 | 02/23/2026 06:22 | 02/25/2026 05:58 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown A and B-phase line fuses (2 of 3) P22 Driftway. Cause: Broken tree limbs took down primary along Kent St, also failed taps at P22 Driftway. Manually opened line fuses P2 Moorland Rd to repair broken pole top pins and poles on Parker Ave, Cliff Ave, Collier Rd, and Moorland Rd. Broken tree limbs also took down primary on Gilson Rd and blew transformer fuses on Cobb Ln. ABB Order Id: 870550, 873689, 872642, 870604, 870585, 874074 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810911 | A
03/27/2026 07:58:48 | NanECo | Bay State South | NANTUCKET | TOM NEVERS RD | CANDLE STREET 101 | 04-101L8 | 15 | OH | 571 | 0 | 54.55 | 36499.06 | 02/23/2026 04:19 | 02/27/2026 16:56 | Physical Interference / Company | Pole - wood |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Phases down at P1 Tom Nevers Rd (solid tapped to Milestone Rd, fuses at P2). Extensive damage from Blizzard 2026, wires down, poles down. ABB Order Id: 871214 ABB Order Id: 874313, 874695, 874298, 871181, 874490, 874602, 874618 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811193 | A
03/27/2026 06:19:45 | MECo | Bay State South | SCITUATE | COUNTRY WAY | SCITUATE SUB | 07-915W36 | 15 | OH | 27 | 0 | 44.97 | 1282.16 | 02/23/2026 05:20 | 02/25/2026 04:50 | Failed Equipment | Cutout - open |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown A and C-phase line fuses (2 of 3) P477 Country Way. Cause: Failed cutout P5 Jenkins Rd. ABB Order Id: 871986, 870198 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810958 | A
03/26/2026 14:32:01 | MECo | Bay State South | HANOVER | WINTER ST | PHILLIPS LANE | 07-95W2 | 15 | OH | 761 | 0 | 0.00 | 21571.05 | 02/23/2026 07:14 | 02/24/2026 21:03 | Tree Contact | Pole - wood |  | WIND | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser lockout P39 Winter St. FLISR operated to restore customers downstream of PTR P27-50 Wampatuck St. Cause: tree fell at P48 Oldham St and broke pole and broke conductors. Manually opened disconnects P33 Winter St and closed PTR P39 Winter, opened loadbreak P57-1 Oldham and closed PTR P27-50 Wampatuck to minimize outage. ABB Order Id: 870808 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840297 | A
03/26/2026 13:38:54 | MECo | Bay State South | HANOVER | WINTER ST | PHILLIPS LANE | 07-95W2 | 15 | OH | 304 | 0 | 1.36 | 413.02 | 02/25/2026 10:41 | 02/25/2026 12:03 | Tree Contact | No failure or Unknown |  | SNOW | M | Y | Y | N | tc |  |  | Y | Rob OBrien;Tim Kane;Jason Cavallaro; | Email (robrien@hanson-ma.gov);Email (Timothy.kane@hanover-ma.gov);Email (jason.cavallaro@hanover-ma.gov); |  |  | Pole top recloser L/O P39 Winter St due to tree branch on 3 phases at P4 Winter St Hanover. Feeder was abnormal from previous outage. All customers downstream of loadbreak P57-1 Oldham St were being carried on 95W3 feeder. ABB Order Id: 874217 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811019 | A
03/26/2026 11:43:51 | MECo | Bay State South | SCITUATE | FIRST PARISH RD | SCITUATE SUB | 07-915W36 | 15 | OH | 1713 | 0 | 36.34 | 61906.86 | 02/23/2026 05:28 | 02/25/2026 12:44 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser P2 First Parish Rd locked out. Cause: Multiple trees down and phases slapping from high winds along First Parish Rd, Front St, and Beaver Dam Rd. FLISR did not operate due to concurrent outage on 915W82 feeder. Manually opened stepdown transformer fuses P3 Edward Foster Rd, disconnects P4 Front St, and PTR P4 Jerico Rd to restore in sections due to further damage. Multiple side taps were out following restoration of mainline. ABB Order Id: 870227 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811063 | A
03/26/2026 09:22:18 | MECo | Bay State South | COHASSET | BEECHWOOD ST | NORTH SCITUATE UNIT 65 | 07-65J1 | 5 |  | 7 | 0 | 36.29 | 254.10 | 02/23/2026 06:19 | 02/24/2026 18:37 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P26 Beechwood St. Cause: tree fell and damaged transformer and pulled secondary wires down at this location. ABB Order Id: 870419 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810772 | A
03/26/2026 08:38:17 | MECo | Bay State South | SCITUATE | H T BAILEY RD | NORTH SCITUATE UNIT 65 | 07-65J1 | 5 | OH | 131 | 0 | 0.00 | 3790.78 | 02/23/2026 07:46 | 02/24/2026 12:42 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown A & B phase fuses on high side of transformer at North Scituate substation. Access to substation was delayed because of snow. Once crew was able to access substation, manually opened 65J1 circuit breaker to de-energize remaining customers. No cause was found on patrol. Outage number reduced for pole top recloser lockout P943 Country Way (event# 8810678). ABB Order Id: 872954 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840264 | A
03/26/2026 06:16:29 | MECo | Bay State South | BROCKTON | OAK ST | AMES SUB | 07-911W25 | 15 | OH | 0 | 0 | 0.00 | 0.00 | 02/25/2026 13:23 | 02/25/2026 13:23 | Failed Equipment | Lightning arrester |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser P12 Oak St tripped and reclosed once due to failed lightning arrestor P40 Oak St, which also blew the associated riser fuse and broke high-side tap, resulting in commercial part power. | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840257 | A
03/25/2026 10:57:34 | MECo | Bay State South | SCITUATE | COUNTRY WAY | NORTH SCITUATE UNIT 65 | 07-65J1 | 5 | OH | 377 | 0 | 35.90 | 12581.37 | 02/23/2026 06:48 | 02/25/2026 02:29 | Tree Contact | Conductors |  | WIND | M | Y | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser lockout P943 Country Way. Cause: tree fell at P152 South Main St and broke multiple sections of wire between P151 and P153 South Main St and damaged disconnects at P151 South Main St. During outage, tree fell at P4 Norman Todd Rd causing wire down. Manually opened line fuse P12 Beechwood St to isolate prior to closing PTR P943 Country Way. Customer count reduced for transformer outage P26 Beechwood St (IDS event#8810772). ABB Order Id: 870613, 874004 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810678 | A
03/25/2026 06:07:29 | MECo | Bay State South | PEMBROKE | CHURCH ST | WATER STREET #910 | 07-910W51 | 15 | OH | 83 | 0 | 0.00 | 2524.10 | 02/23/2026 09:52 | 02/24/2026 22:35 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown B-phase line fuse (1 of 3) P11 Church St and blown line fuse P18 Water St. Cause: Tree fell, took down primary and broke transformer P12 Water St. ABB Order Id: 873053, 871654 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840106 | A
03/24/2026 11:16:30 | MECo | Bay State South | HANOVER | 25 LINE ROW ROW | WATER STREET #910 | 07-910W51 | 15 | OH | 1075 | 0 | 23.04 | 15634.55 | 02/23/2026 09:45 | 02/24/2026 15:06 | Tree Contact | Crossarm |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | 910W51 circuit breaker at Water St sub and pole top recloser P19-50 Rockland St locked out. Cause: Tree fell and broke cross arm P108 Hanover St. FLISR operated successfully, restoring customers between PTRs P4-50 Schoosett St and P19 Oak St. Isolated between load breaks P88 and P113 Hanover St. After restoration of feeder, transformer fuse P22 Spring St was found blown due to a tree branch breaking cutout. ABB Order Id: 871545, 873099 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810590 | A
03/24/2026 10:20:33 | MECo | Bay State South | RANDOLPH | CANTON ST | SOUTH RANDOLPH 97 | 07-97W2 | 5 | OH | 1 | 0 | 32.52 | 37.84 | 02/23/2026 09:41 | 02/24/2026 18:12 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 161 Canton Rd - reattached service. ABB Order Id: 871518, 873956 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810747 | A
03/24/2026 09:33:44 | MECo | Bay State South | RANDOLPH | NILES RD | SOUTH RANDOLPH 97 | 07-97W2 | 5 | OH | 1 | 0 | 38.01 | 38.00 | 02/23/2026 08:13 | 02/24/2026 22:14 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and broke service to 35 Niles Rd - ran new service. ABB Order Id: 871105 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810842 | A
03/24/2026 09:18:56 | MECo | Bay State South | RANDOLPH | CANTON ST | SOUTH RANDOLPH 97 | 07-97W2 | 15 | OH | 15 | 0 | 34.96 | 534.87 | 02/23/2026 07:19 | 02/24/2026 18:16 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P22 Canton St. Cause: Tree fell and broke multiple poles and spans of primary on East Oxbow Ln. ABB Order Id: 870826, 873956 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810757 | A
03/24/2026 09:11:50 | MECo | Bay State South | RANDOLPH | JOHNSON DR | SOUTH RANDOLPH 97 | 07-97W2 | 15 | OH | 49 | 0 | 2.16 | 133.23 | 02/25/2026 13:55 | 02/26/2026 15:06 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Pole top recloser P5-52 Recycle Way locked out due to a broken C-phase tap at P56 Canton St towards P1 Johnson Dr. Manually opened PTR P1 Johnson Dr to replace tap with no load. ABB Order Id: 874368, 874404 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811078 | A
03/24/2026 08:13:13 | MECo | Bay State South | BROCKTON | PEARL ST | BELMONT SUB | 07-98W46 | 5 | OH | 1 | 0 | 28.24 | 28.23 | 02/23/2026 10:34 | 02/24/2026 14:49 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and broke service to 438 Pearl St. ABB Order Id: 871874 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810608 | A
03/24/2026 07:58:38 | MECo | Bay State South | BROCKTON | PLEASANT ST | PARKVIEW SUB. | 07-94W40 | 15 | OH | 15 | 0 | 25.42 | 381.25 | 02/23/2026 07:15 | 02/24/2026 08:40 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P50 Pleasant St. Cause: Unknown. ABB Order Id: 872906 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810458 | A
03/24/2026 07:53:00 | MECo | Bay State South | HANSON | COUNTY RD | PLYMOUTH | 07-93W43 | 5 | OH | 1 | 0 | 27.11 | 27.10 | 02/23/2026 12:43 | 02/24/2026 15:50 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 370 County Rd. ABB Order Id: 872266 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810642 | A
03/24/2026 07:50:52 | MECo | Bay State South | EASTON | FOUNDRY ST | EASTON SUB | 07-92W79 | 5 | OH | 1 | 0 | 0.00 | 10.17 | 02/24/2026 10:04 | 02/24/2026 20:15 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 762 Foundry St. ABB Order Id: 873501 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840072 | A
03/24/2026 07:47:32 | MECo | Bay State South | ABINGTON | BEDFORD ST | PLYMOUTH | 07-93W42 | 5 | OH | 1 | 0 | 0.00 | 11.27 | 02/23/2026 23:43 | 02/24/2026 01:17 | Failed Equipment | Splice |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Neutral splice P24-31 Bedford St to house 272 Bedford St failed. ABB Order Id: 873101, 873279, 873548 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840077 | A
03/24/2026 07:43:41 | MECo | Bay State South | WHITMAN | DANECCA DR | PLYMOUTH | 07-93W42 | 15 |  | 5 | 0 | 0.00 | 131.76 | 02/23/2026 12:52 | 02/24/2026 15:14 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 14:53 |  | N |  |  |  |  | Blown transformer fuse P4 Danecca St. Cause: Unknown. ABB Order Id: 872281 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840076 | A
03/24/2026 07:41:40 | MECo | Bay State South | ABINGTON | BLOCK ST | PLYMOUTH | 07-93W42 | 5 | OH | 1 | 0 | 0.00 | 22.48 | 02/23/2026 12:38 | 02/24/2026 11:07 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Tree fell and took down service to 45 Block St. ABB Order Id: 872223 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840075 | A
03/24/2026 07:39:33 | MECo | Bay State South | ABINGTON | LINWOOD ST | PLYMOUTH | 07-93W42 | 15 |  | 7 | 0 | 0.00 | 199.88 | 02/23/2026 06:34 | 02/24/2026 11:08 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 11:08 |  | N |  |  |  |  | Blown transformer fuse P38 Linwood St due to broken tree limb across cutout and arrestor. ABB Order Id: 872492 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840074 | A
03/24/2026 07:35:39 | MECo | Bay State South | ABINGTON | HANCOCK ST | PLYMOUTH | 07-93W42 | 15 |  | 9 | 0 | 0.00 | 263.85 | 02/23/2026 05:20 | 02/24/2026 10:39 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc | 02/24/2026 10:38 |  | N |  |  |  |  | Transformer tap ripped out of bottom of cutout P81 Hancock St. ABB Order Id: 870196 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840073 | A
03/24/2026 07:09:38 | MECo | Bay State South | EASTON | PURCHASE ST | EASTON SUB | 07-92W54 | 15 | OH | 95 | 0 | 0.00 | 87.14 | 02/23/2026 18:05 | 02/23/2026 19:00 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 00:32 |  | N |  |  |  |  | Blown B and C-phase line fuses (2 of 3) P7 Purchase St. Cause: Unknown. ABB Order Id: 872804 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840070 | A
03/24/2026 06:59:38 | MECo | Bay State South | EASTON | PROSPECT ST | EASTON SUB | 07-92W54 | 15 | OH | 89 | 0 | 0.00 | 1127.48 | 02/23/2026 08:10 | 02/24/2026 04:26 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 04:25 |  | N |  |  |  |  | Blown B-phase line fuse (1 of 3) P48 Prospect St. Cause: Unknown. ABB Order Id: 871154 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840069 | A
03/24/2026 06:49:31 | MECo | Bay State South | EASTON | POQUANTICUT AVE | EASTON SUB | 07-92W78 | 15 | OH | 31 | 0 | 19.36 | 599.85 | 02/23/2026 20:50 | 02/24/2026 16:12 | Tree Contact | Overhead Device Other |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P53 Poquanticut Ave due to broken tree limb at P10 Massapoag Ave knocking phases off pins at four different locations. ABB Order Id: 872976 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810673 | A
03/24/2026 06:38:13 | MECo | Bay State South | EASTON | RANDALL ST | EASTON SUB | 07-92W78 | 5 | OH | 1 | 0 | 0.00 | 51.05 | 02/23/2026 06:45 | 02/25/2026 09:48 | Failed Equipment | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Replaced service to 147 Randall St due to broken neutral - delayed by heavy snow. ABB Order Id: 870592 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8840071 | A
03/24/2026 06:33:52 | MECo | Bay State South | EASTON | RANDALL ST | EASTON SUB | 07-92W78 | 15 | OH | 34 | 0 | 33.19 | 1128.51 | 02/23/2026 06:02 | 02/24/2026 15:13 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P65 Randall St. Cause: Tree fell and took down primary P54 Randall St. Also replaced cutout P65 Randall St. ABB Order Id: 870544 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810618 | A
03/24/2026 06:14:25 | MECo | Bay State South | WEST BRIDGEWATER | WALNUT ST | EASTON SUB | 07-92W44 | 15 | OH | 1 | 0 | 0.96 | 60.07 | 02/23/2026 09:03 | 02/25/2026 21:07 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P4 Walnut St due to broken tree limb. ABB Order Id: 874447, 871347 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811127 | A
03/24/2026 06:10:33 | MECo | Bay State South | EASTON | SHORT ST | EASTON SUB | 07-92W44 | 5 |  | 8 | 0 | 34.00 | 272.00 | 02/23/2026 08:33 | 02/24/2026 18:34 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P4 Short St. Cause: Broken tree limb burnt up on secondary connectors at P6 Short St. ABB Order Id: 871206 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810782 | A
03/24/2026 06:05:55 | MECo | Bay State South | BROCKTON | SUNSET AVE | DUPONT SUB | 07-91W49 | 15 |  | 10 | 0 | 0.00 | 165.06 | 02/23/2026 06:29 | 02/24/2026 12:54 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 12:54 |  | N |  |  |  |  | Blown transformer fuse P3 Sunset Ave. Cause: Unknown. ABB Order Id: 871235 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839936 | A
03/23/2026 12:36:19 | MECo | Bay State South | WHITMAN | TEMPLE ST | DUPONT SUB | 07-91W47 | 15 | OH | 1 | 0 | 0.00 | 19.40 | 02/23/2026 20:24 | 02/24/2026 15:48 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 15:26 |  | N |  |  |  |  | Blown line fuses (2 of 3) P6 Temple St due to phase slap. ABB Order Id: 872951, 873442 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839934 | A
03/23/2026 12:31:29 | MECo | Bay State South | EASTON | BARROWS ST | EASTON SUB | 07-92W43 | 15 | OH | 15 | 0 | 33.94 | 509.03 | 02/23/2026 09:47 | 02/24/2026 19:43 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown C-phase line fuse (1 of 3) P1 Barrows St. Cause: Broken tree limb P1 Barrows St. ABB Order Id: 873097 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810812 | A
03/23/2026 12:26:20 | MECo | Bay State South | EASTON | CENTER ST | EASTON SUB | 07-92W43 | 15 | OH | 5 | 0 | 32.44 | 162.17 | 02/23/2026 04:56 | 02/24/2026 13:23 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses (2 of 3) P53 Center St. Cause: Broken tree limb on primary P53-30 Gary Ln. ABB Order Id: 870089 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810570 | A
03/23/2026 12:20:02 | MECo | Bay State South | BROCKTON | WARREN AVE | DUPONT SUB | 07-91W48 | 15 | OH | 85 | 0 | 27.60 | 2350.11 | 02/23/2026 06:04 | 02/24/2026 09:44 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P9 Warren Ave. Cause: Broken tree limb took down primary between P4 and P4-1 Warren Ave. ABB Order Id: 870374 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810462 | A
03/23/2026 12:09:56 | MECo | Bay State South | BROCKTON | QUINCY ST | DUPONT SUB | 07-91W47 | 15 |  | 7 | 0 | 0.00 | 64.46 | 02/23/2026 06:47 | 02/24/2026 13:01 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 13:00 |  | N |  |  |  |  | Blown transformer fuse P33 Quincy St. Cause: Unknown. ABB Order Id: 870600 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839930 | A
03/23/2026 12:01:18 | MECo | Bay State South | WHITMAN | TEMPLE ST | DUPONT SUB | 07-91W47 | 15 |  | 15 | 0 | 7.64 | 114.50 | 02/23/2026 09:52 | 02/23/2026 17:31 | Failed Equipment | Cutout door/fuse holder |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown transformer fuse P51 Temple St. Cause: Failed Kierney door. ABB Order Id: 871622 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810249 | A
03/23/2026 11:51:17 | MECo | Bay State South | STOUGHTON | TURNPIKE ST | STOUGHTON | 07-913W17 | 15 | OH | 99 | 0 | 0.00 | 3168.25 | 02/23/2026 03:58 | 02/24/2026 11:58 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 11:41 |  | N |  |  |  |  | Blown B-phase line fuse (1 of 3) P26 Turnpike St. Cause: Unknown. ABB Order Id: 869982 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839920 | A
03/23/2026 11:44:03 | MECo | Bay State South | STOUGHTON | CENTRAL ST | STOUGHTON | 07-913W47 | 15 | OH | 3 | 0 | 0.00 | 56.16 | 02/23/2026 04:16 | 02/24/2026 12:06 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuses P130 Central St. Cause: Tree fell on primary P4 McCormick Ter. ABB Order Id: 869983 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839921 | A
03/23/2026 11:29:59 | MECo | Bay State South | STOUGHTON | SUMNER ST | STOUGHTON | 07-913W67 | 15 | OH | 73 | 0 | 25.45 | 39.12 | 02/23/2026 14:24 | 02/24/2026 15:53 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P68 Sumner St. Cause: Tree fell and broke P14 Cedar St. ABB Order Id: 872488 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810647 | A
03/23/2026 10:30:42 | MECo | Bay State South | HALIFAX | HOLMES ST | MILL STREET SUB | 07-912W75 | 15 | OH | 3 | 0 | 33.75 | 101.20 | 02/23/2026 10:15 | 02/24/2026 20:00 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse P22 Holmes St. Cause: Tree fell and broke primary P22-30 Holmes St. ABB Order Id: 872931 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810820 | A
03/23/2026 10:22:54 | MECo | Bay State South | HALIFAX | FRANKLIN ST | MILL STREET SUB | 07-912W75 | 5 | OH | 42 | 0 | 28.08 | 1178.80 | 02/23/2026 06:51 | 02/24/2026 10:55 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown stepdown transformer fuse P13 Franklin St. Cause: Tree fell and took down primary P22 Franklin St. ABB Order Id: 870682 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810500 | A
03/23/2026 10:10:35 | MECo | Bay State South | HALIFAX | HOLMES ST | MILL STREET SUB | 07-912W75 | 15 | OH | 60 | 0 | 30.50 | 1727.25 | 02/23/2026 06:07 | 02/24/2026 11:25 | Tree Contact | Transformer O/H conv. |  | BLIZ | M | N | Y | N | tc |  |  | N |  |  |  |  | Blown line fuse (1 of 2) P57 Holmes St and blown transformer fuse P19 Annawon Dr. Cause: Tree fell, broke transformer P19 Annawon Dr and took down service to 98 Annawon Dr - electrician needed. ABB Order Id: 872930 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810536 | A
03/23/2026 08:07:32 | MECo | Bay State South | BRIDGEWATER | R.O.W. 2 X X | MILL STREET SUB | 07-912W75 | 15 | OH | 233 | 0 | 4.78 | 3619.60 | 02/23/2026 10:13 | 02/24/2026 01:30 | Failed Equipment | Tap |  | BLIZ | M | Y | Y | N | tc |  |  | Y | Joao Chaves;Jason Viveiros;Christopher D. Delmonte; | Email (chief@police.halifax.ma.us);Email (chief@fire.halifax.ma.us);Email (cdelmonte@bridgewaterma.org); |  |  | Failed B-phase tap to disconnects P100 Plymouth St. FLISR operated successfully, restoring all B-phase customers beyond pole top recloser P2 Thompson St - customer count reduced to reflect concurrent downstream outages. Manually opened 912W75 circuit breaker at Mill St sub to replace tap. ABB Order Id: 872215, 871794 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839345 | A
03/20/2026 16:40:55 | MECo | Bay State South | SWANSEA | WILBUR AVE | SWANSEA 11 | 05-11W83 | 15 | OH | 26 | 0 | 1.54 | 39.87 | 02/25/2026 09:32 | 02/25/2026 11:05 | Failed Equipment | Overhead Device Other |  | NORM | M | N | Y | N | tc | 02/25/2026 10:15 |  | N |  |  |  |  | Blown line fuse P73 Wilbur Ave. At P1 Oban Way, phase off the pin. ABB Order Id: 874186 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811006 | A
03/20/2026 16:30:26 | MECo | Bay State South | SWANSEA | PINEHURST AVE | SWANSEA 11 | 05-11W83 | 15 | OH | 77 | 0 | 32.52 | 2242.45 | 02/23/2026 08:06 | 02/24/2026 16:37 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc | 02/24/2026 11:30 |  | N |  |  |  |  | Blown line fuse at P3 Pinehurst Ave caused by down tree limb on P10 Oceanview Ave. Replaced two poles P10 and P11. Blizzard 2026. ABB Order Id: 873511 ABB Order Id: 873743, 872969, 871705 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810623 | A
03/20/2026 16:23:01 | MECo | Bay State South | SWANSEA | HARBOR RD | SWANSEA 11 | 05-11W83 | SY | OH | 1 | 0 | 25.63 | 25.62 | 02/23/2026 08:07 | 02/24/2026 09:44 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 08:30 |  | N |  |  |  |  | Tree came down on service drop at 121 Harbor Rd. Broke neutral and ripped hot legs off secondaries. Replaced service from P6 to house. ABB Order Id: 871072 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810450 | A
03/20/2026 16:18:26 | MECo | Bay State South | SWANSEA | BARTON RD | SWANSEA 11 | 05-11W83 | 15 | OH | 107 | 0 | 1.80 | 190.82 | 02/23/2026 03:18 | 02/23/2026 05:06 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 04:43 |  | Y | Police Dispatcher; | Email (firedispatch@swanseama.gov); |  |  | Blown line fuse P1 Pearse Rd. Removed tree on wires at pole 14 Barton. Blizzard 2026. ABB Order Id: 869934 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810097 | A
03/20/2026 16:14:07 | MECo | Bay State South | SWANSEA | NEW MEADOW RD | SWANSEA 11 | 05-11W81 | 15 | OH | 7 | 0 | 23.07 | 161.47 | 02/23/2026 11:22 | 02/24/2026 10:27 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 09:30 |  | N |  |  |  |  | Blown line fuse at P1 New Meadow Rd. Roads are not plowed. Tree limb at P3. Refused 25K at P1. Blizzard 2026. ABB Order Id: 872029 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810482 | A
03/20/2026 16:11:48 | MECo | Bay State South | SWANSEA | LAZYWOOD LN | SWANSEA 11 | 05-11W81 | SY | OH | 1 | 0 | 19.15 | 19.15 | 02/23/2026 14:27 | 02/24/2026 09:36 | Tree Contact | Connector |  | WIND | M | N | Y | N | tc | 02/24/2026 08:30 |  | N |  |  |  |  | Tree took down service to house 96 Lazywood Ln, also needs electrician. ABB Order Id: 872487 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810447 | A
03/20/2026 16:09:48 | MECo | Bay State South | SWANSEA | STONEY HILL RD | SWANSEA 11 | 05-11W81 | 15 | OH | 159 | 0 | 7.27 | 1155.40 | 02/23/2026 08:44 | 02/23/2026 16:00 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/23/2026 15:00 |  | Y | Police Dispatcher; | Email (firedispatch@swanseama.gov); |  |  | Blown line fuse P1 Stoney Hill Rd 65K. Large tree on primary at P3 Stoney Hill Rd. Road has not yet been plowed. Needed tree crew. Blizzard 2026. ABB Order Id: 871246 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810221 | A
03/20/2026 15:41:05 | MECo | Bay State South | SCITUATE | COUNTRY WAY | SCITUATE UNIT 15 | 07-15J1 | SY | OH | 1 | 0 | 54.17 | 54.17 | 02/23/2026 05:10 | 02/25/2026 11:20 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc | 02/25/2026 10:30 |  | N |  |  |  |  | No power to address 537 Country Way. Cause: tree fell and damaged service between P885-30 Country Way and house.\r\n\r\nService repaired. Restored 11:18 ABB Order Id: 874142, 874001 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811005 | A
03/20/2026 15:39:35 | NanECo | Bay State South | NANTUCKET | CROOKED LN | CANDLE STREET 101 | 04-101L6 | 5 | OH | 1 | 0 | 31.38 | 31.37 | 02/25/2026 08:04 | 02/26/2026 15:27 | Failed Equipment | Connector |  | NORM | M | N | Y | N | tc | 02/26/2026 14:00 |  | N |  |  |  |  | Service drop down to 21 Crooked Lane. ABB Order Id: 874144 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811202 | A
03/20/2026 15:29:19 | NanECo | Bay State South | NANTUCKET | MAIN ST | CANDLE STREET 101 | 04-101L6 | 15 | OH | 826 | 0 | 52.01 | 28967.18 | 02/23/2026 10:53 | 02/25/2026 14:54 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 08:00 |  | N |  |  |  |  | Pole top recloser at P18 Main St locked out due to trees taking down primary between P6 and P10 Madaket Rd. Note: earlier, P3 Eel Point PTR had locked out (see other IDS event) so those customers were not affected. Also Warrens' Landing / Blue Heron SWGR fuses had blown earlier, so customer count is reduced (see IDS event 8839365). Miscellaneous line and transformers were out longer as repairs were made. Note: customer count reduced by previously blown transformer fuse on Crooked Lane. ABC ABB Order Id: 871958 ABB Order Id: 874082 ABB Order Id: 874026 ABB Order Id: 874000 Blown transformer fuse P1 Cambridge St cause was ice on wires. ABB Order Id: 874501 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810915 | A
03/20/2026 15:27:00 | MECo | Bay State South | SCITUATE | FAIRVIEW AVE | SCITUATE UNIT 15 | 07-15J1 | SY | OH | 1 | 0 | 17.76 | 17.75 | 02/24/2026 16:43 | 02/25/2026 10:29 | Tree Contact | Connector |  | NORM | M | N | Y | N | tc | 02/25/2026 09:45 |  | N |  |  |  |  | No power to 26 Utility Rd. Cause: tree limb pulled service off house. ABB Order Id: 873810 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810996 | A
03/20/2026 15:24:43 | MECo | Bay State South | SCITUATE | CHIEF JUSTICE CUSHING HWY | SCITUATE UNIT 15 | 07-15J1 | 5 |  | 1 | 0 | 2.31 | 2.30 | 02/25/2026 13:13 | 02/25/2026 15:31 | Tree Contact | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/25/2026 15:00 |  | N |  |  |  |  | Blown transformer fuses P105-32 R/W off Chief Justice Cushing Hwy (3 of 3). Cause: tree branch. ABB Order Id: 874347 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811067 | A
03/20/2026 15:14:15 | NanECo | Bay State South | NANTUCKET | BLUE HERON WAY | CANDLE STREET 101 | 04-101L6 | 15 | OH | 594 | 0 | 104.40 | 29568.23 | 02/23/2026 06:53 | 02/27/2026 15:18 | Physical Interference / Company | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 12:00 |  | N |  |  |  |  | Blown fuses at Warren Landing / Blue Heron SWGR. Phases down on North Cambridge St. Ice / snow buildup on wires. Blizzard 2026. ABB Order ID 870061 Blown line fuse P3 Washington St cause pole broke due to weather. ABB Order Id: 874449, 874543 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839365 | A
03/20/2026 15:12:38 | NanECo | Bay State South | NANTUCKET | CROOKED LN | CANDLE STREET 101 | 04-101L6 | 5 |  | 10 | 0 | 37.09 | 370.83 | 02/23/2026 06:45 | 02/24/2026 19:50 | Physical Interference / Company | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 18:00 |  | N |  |  |  |  | Blown transformer fuse P8 Crooked Lane. Wires down due to snow and ice buildup. Blizzard 2026. ABB Order ID: 871958, 874026 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839366 | A
03/20/2026 15:10:36 | MECo | Bay State South | SCITUATE | CURTIS ST | SCITUATE UNIT 15 | 07-15J1 | SY | OH | 1 | 0 | 29.65 | 29.63 | 02/23/2026 12:06 | 02/24/2026 17:45 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 16:45 |  | N |  |  |  |  | No power to address 14 Curtis St. Cause: tree fell and damaged service to house. ABB Order Id: 872140 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810734 | A
03/20/2026 14:26:05 | NanECo | Bay State South | NANTUCKET | EEL POINT RD | CANDLE STREET 101 | 04-101L6 | 15 | OH | 287 | 0 | 85.43 | 20051.88 | 02/23/2026 06:14 | 02/26/2026 19:40 | Failed Equipment | Crossarm |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 18:00 |  | N |  |  |  |  | Pole top recloser lockout at P3 Eel Point Rd. Phases down, multiple locations and many broken crossarms. Ice buildup on wires. Blizzard 2026. Note: Due to GIS not being up to date at Blue Heron/Warren's landing SWGR, section (L) added/affected. Note: Warren Landing SWGR had transferred to the Madeket source before the Eel Point outage, so customer count is reduced. ABB Order Id: 870026 ABB Order Id: 870410 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811235 | A
03/20/2026 14:25:07 | MECo | Bay State South | SCITUATE | BRANCH ST | SCITUATE UNIT 15 | 07-15J1 | 15 | OH | 29 | 0 | 33.61 | 974.40 | 02/23/2026 10:04 | 02/24/2026 19:41 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc | 02/24/2026 18:30 |  | N |  |  |  |  | Blown line fuse P1 Branch St. Cause: tree branch fell and broke primary on Branch St. ABB Order Id: 871760 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810809 | A
03/20/2026 13:59:58 | MECo | Bay State South | SCITUATE | FIRST PARISH RD | SCITUATE UNIT 15 | 07-15J1 | 5 | OH | 28 | 0 | 6.52 | 182.47 | 02/23/2026 11:23 | 02/23/2026 17:55 | Tree Contact | Overhead Device Other |  | WIND | M | N | Y | N | tc | 02/23/2026 16:45 |  | N |  |  |  |  | Blown line fuse P123 First Parish Rd. Cause: tree limb fell and pulled primary off insulators at P5 and P6 Pheasant Hill Dr. ABB Order Id: 872072 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810271 | A
03/20/2026 13:52:41 | MECo | Bay State South | SCITUATE | DREAMWOLD RD | SCITUATE UNIT 15 | 07-15J1 | SY | OH | 1 | 0 | 30.07 | 30.07 | 02/23/2026 10:03 | 02/24/2026 16:07 | Tree Contact | Connector |  | OTHR | M | N | Y | N | tc | 02/24/2026 15:30 |  | N |  |  |  |  | No power to 29 Dreamwold Rd. Cause: tree branch pulled service off house. ABB Order Id: 871712 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810655 | A
03/20/2026 13:17:03 | NanECo | Bay State South | NANTUCKET | BLUE HERON WAY | CANDLE STREET 101 | 04-101L6 | 15 | OH | 234 | 0 | 2.05 | 479.70 | 02/23/2026 03:57 | 02/23/2026 06:00 | Physical Interference / Company | Conductors |  | BLIZ | M | N | Y | N | tc | 02/23/2026 05:00 |  | N |  |  |  |  | Blown switchgear fuse (1 of 3, B phase) at Warren's Landing SWGR. Phase down on North Cambridge St due to ice buildup. Blizzard 2026. ABB Order ID: 870061 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839351 | A
03/20/2026 12:41:37 | MECo | Bay State South | SCITUATE | CAIRNSLEA LN | SCITUATE UNIT 15 | 07-15J1 | 5 |  | 3 | 0 | 32.78 | 98.30 | 02/23/2026 09:03 | 02/24/2026 17:50 | Failed Equipment | Cutout - open |  | WIND | M | N | Y | N | tc | 02/24/2026 17:15 |  | N |  |  |  |  | Blown transformer fuse P1 Cairnslea Lane. Cause: failed cutout. PABB Order Id: 871349 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810733 | A
03/20/2026 12:33:47 | MECo | Bay State South | SCITUATE | COUNTRY WAY | SCITUATE UNIT 15 | 07-15J1 | 5 | OH | 183 | 0 | 38.93 | 7119.80 | 02/23/2026 05:10 | 02/24/2026 20:06 | Tree Contact | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/24/2026 17:30 |  | N |  |  |  |  | Blown B and C phase line fuses P868 Country Way and blown B phase line fuse P544 Country Way. Cause: tree on wires on Country Way. Crew closed fuse at P544 Country Way and close fuses at P868 Country Way to restore all customers. ABB Order Id: 870176, 870191, 872454, 870230 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810831 | A
03/20/2026 11:54:16 | MECo | Bay State South | BRIDGEWATER | ROBERTS RD | MILL STREET SUB | 07-912W74 | 15 |  | 5 | 0 | 23.56 | 117.75 | 02/23/2026 09:51 | 02/24/2026 09:25 | Failed Equipment | Tap |  | BLIZ | M | N | Y | N | tc | 02/24/2026 08:00 |  | N |  |  |  |  | Broken transformer tap P6 Roberts Rd. ABB Order Id: 871581 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810463 | A
03/20/2026 09:53:42 | MECo | Bay State South | BRIDGEWATER | FLAGG ST | MILL STREET SUB | 07-912W55 | 15 | OH | 173 | 0 | 13.22 | 1345.35 | 02/23/2026 06:30 | 02/23/2026 19:43 | Tree Contact | Overhead Device Other |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 17:00 |  | Y | Christopher D. Delmonte; | Email (cdelmonte@bridgewaterma.org); |  |  | Blown line fuse P58 Summer St. Cause: Tree fell P58 Summer St, knocked phase off pin. Manually opened upstream C-phase line fuse (1 of 3) P29 Flagg St for worker safety to tie in phase due to strong winds. ABB Order Id: 873083, 873089, 873085, 873088, 873082, 873081 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839320 | A
03/20/2026 08:43:16 | MECo | Bay State South | BRIDGEWATER | AUBURN ST | MILL STREET SUB | 07-912W55 | 15 | OH | 4 | 0 | 15.02 | 60.00 | 02/23/2026 18:23 | 02/24/2026 09:24 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 09:00 |  | N |  |  |  |  | Blown line fuse P56 Auburn St due to broken tree limb on primary P56-30 Auburn St. ABB Order Id: 872922 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810469 | A
03/20/2026 08:32:05 | MECo | Bay State South | BRIDGEWATER | LAUREL ST | MILL STREET SUB | 07-912W55 | 15 | OH | 110 | 0 | 12.70 | 1395.17 | 02/23/2026 06:15 | 02/23/2026 18:57 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 15:00 |  | Y | Christopher D. Delmonte; | Email (cdelmonte@bridgewaterma.org); |  |  | TripSaver P1 Laurel St found open. Cause: Unknown. ABB Order Id: 870515 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839319 | A
03/20/2026 08:18:23 | MECo | Bay State South | BRIDGEWATER | VERNON ST | MILL STREET SUB | 07-912W55 | 15 | OH | 174 | 0 | 24.58 | 4274.60 | 02/23/2026 08:26 | 02/24/2026 09:01 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 07:30 |  | Y | Christopher D. Delmonte; | Email (cdelmonte@bridgewaterma.org); |  |  | Blown B-phase line fuse (1 of 3) P99 Vernon St. Cause: Unknown. ABB Order Id: 871141, 873390 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810436 | A
03/20/2026 07:55:40 | MECo | Bay State South | E. BRIDGEWATER | R.O.W. 4 X X | MILL STREET SUB | 07-912W22 | 15 | OH | 8 | 0 | 27.75 | 221.87 | 02/23/2026 06:27 | 02/24/2026 10:12 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 09:30 |  | Y | John Dzialo; | Email (jdzialo@eastbridgewaterma.gov); |  |  | Blown C-phase line fuses (1 of 3) P50 R/W off East St and P6 Leo Way. Cause: Unknown. ABB Order Id: 870492 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810473 | A
03/20/2026 07:49:38 | MECo | Bay State South | BRIDGEWATER | ALDRICH RD | MILL STREET SUB | 07-912W21 | 15 | OH | 119 | 0 | 18.69 | 2223.32 | 02/23/2026 08:39 | 02/24/2026 03:20 | Unknown | Conductors |  | BLIZ | M | N | Y | N | tc | 02/23/2026 14:58 |  | N |  |  |  |  | Blown A-phase line fuse (1 of 3) P3 Aldrich Rd due to damaged primary along Aldrich Rd. Cause: Unknown. ABB Order Id: 871231 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839317 | A
03/20/2026 07:32:00 | MECo | Bay State South | BROCKTON | ADDISON ST | AMES SUB | 07-911W25 | 5 | OH | 1 | 0 | 27.46 | 27.45 | 02/23/2026 09:20 | 02/24/2026 12:48 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 10:41 |  | N |  |  |  |  | Tree fell and took down service to 100 Addison St. ABB Order Id: 871417 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839316 | A
03/20/2026 07:28:59 | MECo | Bay State South | BRIDGEWATER | UNION ST | MILL STREET SUB | 07-912W21 | 15 | OH | 1753 | 0 | 6.89 | 12066.48 | 02/23/2026 06:44 | 02/23/2026 13:38 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 08:44 |  | Y | Christopher D. Delmonte;, Christopher D. Delmonte; | Email (cdelmonte@bridgewaterma.org);, Email (cdelmonte@bridgewaterma.org); |  |  | Pole top recloser P27 Oak St tripped and reclosed, and sectionalizer P6 Union St locked out. Patrol found no cause -- blizzard in area. ABB Order Id: 871703 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810182 | A
03/20/2026 06:57:46 | MECo | Bay State South | BROCKTON | GREEN ST | AMES SUB | 07-911W13 | 15 |  | 40 | 0 | 14.78 | 590.67 | 02/23/2026 17:43 | 02/24/2026 08:30 | Failed Equipment | Tap |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 08:00 |  | N |  |  |  |  | Broken transformer tap P8 Green St from high wind and ice buildup. ABB Order Id: 872778 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810464 | A
03/20/2026 06:16:50 | MECo | Bay State South | E. BRIDGEWATER | LORI LN | EAST BRIDGEWATER SUB | 07-797W42 | SY | OH | 1 | 0 | 27.66 | 27.65 | 02/23/2026 09:00 | 02/24/2026 12:40 | Tree Contact | Connector |  | BLIZ | M | N | Y | N | tc | 02/24/2026 12:05 |  | N |  |  |  |  | Broken tree limb took down service to 49 Lori Ln. ABB Order Id: 871332 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810532 | A
03/20/2026 06:14:58 | MECo | Bay State South | E. BRIDGEWATER | ELM ST | EAST BRIDGEWATER SUB | 07-797W42 | 15 | OH | 52 | 0 | 31.51 | 1638.00 | 02/23/2026 06:57 | 02/24/2026 14:28 | Physical Interference / Other | Pole - wood |  | BLIZ | M | N | Y | N | tc | 02/23/2026 06:57 |  | N |  |  |  |  | Manually opened line fuse P27 Elm St to de-energize broken P5 Elm St due to MVA. Winds were too strong to set a new pole until the following day. ABB Order Id: 871957 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810596 | A
03/20/2026 05:59:25 | MECo | Bay State South | HANSON | FRANKLIN ST | EAST BRIDGEWATER SUB | 07-797W29 | 15 | OH | 218 | 0 | 16.79 | 3658.77 | 02/23/2026 06:11 | 02/23/2026 22:59 | Tree Contact | Crossarm |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 12:20 |  | Y | John Dzialo; | Email (jdzialo@eastbridgewaterma.gov); |  |  | Blown line fuses P22 Franklin St. Cause: Tree fell and broke cross arm P220 Central St and knocked phases off pins. ABB Order Id: 870426 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839278 | A
03/19/2026 13:15:39 | MECo | Bay State South | WEYMOUTH | WHARF ST | EAST WEYMOUTH 9 | 07-9W1 | 15 | OH | 696 | 0 | 4.19 | 2903.46 | 02/23/2026 05:24 | 02/23/2026 09:35 | Adverse Environment | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 08:30 |  | N |  |  |  |  | 9W1 circuit breaker lockout at East Weymouth substation. FLISR scheme operated successfully, restoring between pole top recloser at P3 Unicorn Ave and PTR P14 Green St. ABB Order Id: 870215 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810122 | A
03/19/2026 12:38:50 | MECo | Bay State South | E. BRIDGEWATER | HUDSON ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 | OH | 27 | 0 | 6.69 | 180.45 | 02/23/2026 09:48 | 02/23/2026 16:30 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 14:30 |  | Y | John Dzialo; | Email (jdzialo@eastbridgewaterma.gov); |  |  | Blown C-phase line fuse (1 of 3) P6 Hudson St. Cause: Unknown. ABB Order Id: 871561 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839247 | A
03/19/2026 12:35:20 | MECo | Bay State South | PEMBROKE | UNION ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 | OH | 52 | 0 | 23.55 | 1224.60 | 02/23/2026 09:26 | 02/24/2026 09:00 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 08:30 |  | N |  |  |  |  | Blown line fuse P6 Union St. Cause: Broken tree limb on primary P24 Plymouth St. ABB Order Id: 871441 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839268 | A
03/19/2026 12:25:56 | MECo | Bay State South | HANSON | PHILLIPS ST | EAST BRIDGEWATER SUB | 07-797W24 | SY | OH | 1 | 0 | 22.85 | 22.83 | 02/23/2026 16:09 | 02/24/2026 15:00 | Tree Contact | Pole - wood |  | BLIZ | M | N | Y | N | tc | 02/24/2026 09:52 |  | N |  |  |  |  | Tree fell, broke P15-1 Phillips St and took down service to 185 Phillips St. Ran new service, electrician needed. ABB Order Id: 872657 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810716 | A
03/19/2026 12:22:09 | MECo | Bay State South | HALIFAX | HOLMES ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 | OH | 40 | 0 | 23.81 | 952.00 | 02/23/2026 11:00 | 02/24/2026 10:48 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 10:00 |  | N |  |  |  |  | Blown line fuse P6 Holmes St. Cause was a tree branch on wire at P11 McClelland Rd. ABB Order Id: 871996 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810510 | A
03/19/2026 12:19:53 | MECo | Bay State South | PEMBROKE | PLYMOUTH ST | EAST BRIDGEWATER SUB | 07-797W24 | 5 | OH | 1 | 0 | 32.75 | 32.73 | 02/23/2026 10:25 | 02/24/2026 19:10 | Tree Contact | Pole - wood |  | NORM | M | N | Y | N | tc | 02/24/2026 18:18 |  | N |  |  |  |  | Tree fell, broke top of P292-32 Plymouth St and took down service to 252 Plymouth St. ABB Order Id: 871841 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810807 | A
03/19/2026 12:15:57 | MECo | Bay State South | HANSON | BAKER ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 |  | 7 | 0 | 29.17 | 204.17 | 02/23/2026 08:53 | 02/24/2026 14:04 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 14:04 |  | N |  |  |  |  | Blown transformer fuse P2 Baker St due to broken tree limb. ABB Order Id: 871285 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810654 | A
03/19/2026 12:14:15 | MECo | Bay State South | HALIFAX | PRINCETON ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 |  | 1 | 0 | 28.24 | 28.23 | 02/23/2026 07:20 | 02/24/2026 11:34 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 11:11 |  | N |  |  |  |  | Blown transformer fuse P6-33 Princeton St. Cause: Unknown. ABB Order Id: 870828 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839263 | A
03/19/2026 12:10:46 | MECo | Bay State South | HANSON | HIGH ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 | OH | 3 | 0 | 28.83 | 86.50 | 02/23/2026 08:09 | 02/24/2026 13:00 | Tree Contact | Overhead Device Other |  | NORM | M | N | Y | N | tc | 02/24/2026 10:52 |  | N |  |  |  |  | Blown line fuse P39 High St. Cause: Tree fell and knocked phase off pin P3 High St off P39. ABB Order Id: 871083 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810585 | A
03/19/2026 11:33:55 | MECo | Bay State South | HANSON | R.O.W. R.O. | EAST BRIDGEWATER SUB | 07-797W24 | 15 | OH | 72 | 0 | 28.56 | 2055.60 | 02/23/2026 07:14 | 02/24/2026 11:48 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 09:47 |  | N |  |  |  |  | Pole top recloser P85 Main St tripped and reclosed once, and blown A-phase line fuse (1 of 3) P349 in R/W off Monponsett St. Cause: Unknown. ABB Order Id: 870870 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810538 | A
03/19/2026 11:22:06 | MECo | Bay State South | PEMBROKE | ELMER ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 | OH | 22 | 0 | 32.81 | 721.60 | 02/23/2026 06:34 | 02/24/2026 15:23 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 13:00 |  | N |  |  |  |  | Blown line fuse P13 Elmer St. Cause: Broken tree limb on primary along Elmer St. ABB Order Id: 870707 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810625 | A
03/19/2026 11:08:23 | MECo | Bay State South | HALIFAX | OAK ST | EAST BRIDGEWATER SUB | 07-797W24 | 15 | OH | 27 | 0 | 1.45 | 39.15 | 02/23/2026 01:27 | 02/23/2026 02:55 | Tree Contact | Overhead Device Other |  | BLIZ | M | N | Y | N | tc | 02/23/2026 02:15 |  | N |  |  |  |  | Blown line fuse P330 Oak St. Cause: Broken tree limb knocked phase off pin on Oak Pl. ABB Order Id: 869911 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810089 | A
03/19/2026 10:09:25 | MECo | Bay State South | E. BRIDGEWATER | LORRAINE DR | EAST BRIDGEWATER SUB | 07-797W23 | SY | OH | 1 | 0 | 9.83 | 9.82 | 02/24/2026 08:04 | 02/24/2026 17:54 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 15:00 |  | N |  |  |  |  | Tree fell and took down service to 100 Lorraine Dr. ABB Order Id: 873372 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810735 | A
03/19/2026 10:07:27 | MECo | Bay State South | E. BRIDGEWATER | UNION ST | EAST BRIDGEWATER SUB | 07-797W23 | SY | OH | 1 | 0 | 26.05 | 26.05 | 02/23/2026 14:02 | 02/24/2026 16:05 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 14:00 |  | N |  |  |  |  | Tree fell and took down service to 275 Thayer Ave. ABB Order Id: 872446, 873343 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810659 | A
03/19/2026 09:59:37 | MECo | Bay State South | E. BRIDGEWATER | UNION ST | EAST BRIDGEWATER SUB | 07-797W23 | 15 | OH | 500 | 0 | 7.31 | 3650.00 | 02/23/2026 05:55 | 02/23/2026 13:14 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 13:05 |  | Y | John Dzialo; | Email (jdzialo@eastbridgewaterma.gov); |  |  | 797W23 circuit breaker at East Bridgewater sub tripped and reclosed twice, and pole top recloser P64 Union St locked out. Cause: Broken tree limb P75 Union St. ABB Order Id: 870315 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810289 | A
03/19/2026 09:31:21 | MECo | Bay State South | WEST BRIDGEWATER | S ELM ST | EAST BRIDGEWATER SUB | 07-797W20 | 15 | OH | 30 | 0 | 32.81 | 984.00 | 02/23/2026 04:46 | 02/24/2026 13:34 | Tree Contact | Overhead Device Other |  | BLIZ | M | N | Y | N | tc | 02/24/2026 11:00 |  | N |  |  |  |  | Blown line fuse P2 S Elm St. Cause: Phase off pin P14 S Elm St due to fallen tree. ABB Order Id: 870048 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810558 | A
03/19/2026 09:25:09 | MECo | Bay State South | WEST BRIDGEWATER | UNION ST | EAST BRIDGEWATER SUB | 07-797W19 | 15 |  | 8 | 0 | 26.42 | 211.33 | 02/23/2026 08:28 | 02/24/2026 10:54 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 09:40 |  | N |  |  |  |  | Blown transformer fuse P2 Union St. Cause: Unknown. ABB Order Id: 872375 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839233 | A
03/19/2026 09:12:01 | NanECo | Bay State South | NANTUCKET | HUMMOCK POND RD | CANDLE STREET 101 | 04-101L5 | 15 | OH | 22 | 0 | 43.66 | 960.30 | 02/23/2026 09:21 | 02/25/2026 05:00 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/25/2026 04:00 |  | N |  |  |  |  | Blown line fuse at P11 Hummock Pond Rd due to storm conditions, ice buildup on wires sagging into neutral. Blizzard 2026. ABB Order Id: 874044 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810920 | A
03/19/2026 09:02:32 | NanECo | Bay State South | NANTUCKET | HUMMOCK POND RD | CANDLE STREET 101 | 04-101L5 | 15 | OH | 495 | 0 | 78.30 | 21767.32 | 02/23/2026 05:47 | 02/26/2026 12:05 | Physical Interference / Company | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 08:00 |  | N |  |  |  |  | Blown 2 of 3 line fuses at P13 Hummock Pond Rd. Refused 2 blown fuses 2/24 at 11:15. Cause was heavy weight of ice caused conductors swinging in the wind to break. Bartlett Farms Rd P1 100k fuses were open longer for more repairs. Blizzard 2026. ABB Order Id: 873505, 874143, 871155 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811195 | A
03/19/2026 08:43:33 | NanECo | Bay State South | NANTUCKET | HUMMOCK POND RD | CANDLE STREET 101 | 04-101L5 | 15 | OH | 516 | 0 | 67.61 | 18854.77 | 02/23/2026 08:01 | 02/26/2026 03:38 | Physical Interference / Company | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 08:45 |  | N |  |  |  |  | Pole top recloser trip and reclose at P2 Milk St at 8:02. Two phases down at P2 Hummock Pond Rd. Manually opened loadbreak at P10 Hummock Pond Rd to make repairs. Ice covered wires blowing together in the wind. ABB Order Id: 871365 Broken cutout tap at P5 Somerset Rd. Replaced tap to restore customers. ABB Order Id: 874055 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810881 | A
03/19/2026 08:11:01 | MECo | Bay State South | BROCKTON | MAIN ST | EAST BRIDGEWATER SUB | 07-797W19 | 15 | OH | 48 | 0 | 1.07 | 51.20 | 02/23/2026 03:23 | 02/23/2026 04:27 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/23/2026 03:45 |  | N |  |  |  |  | Blown C-phase fuse (1 of 3) P125 Main St. Cause: Unknown. ABB Order Id: 869935 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810092 | A
03/19/2026 08:02:19 | MECo | Bay State South | BRIDGEWATER | BROOKSIDE DR | EAST BRIDGEWATER SUB | 07-797W1 | 15 | OH | 27 | 0 | 24.70 | 666.45 | 02/23/2026 09:26 | 02/24/2026 10:08 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 09:30 |  | N |  |  |  |  | Blown line fuse P17 Brookside Dr. Cause: Broken tree limb fell on primary P22 Grange Park. ABB Order Id: 871500 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810468 | A
03/19/2026 07:40:07 | MECo | Bay State South | BRIDGEWATER | SUMMER ST | EAST BRIDGEWATER SUB | 07-797W1 | 15 | OH | 39 | 0 | 3.68 | 143.00 | 02/23/2026 02:27 | 02/23/2026 06:08 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/23/2026 04:00 |  | N |  |  |  |  | Blown line fuse P25 Summer St. Cause: Tree fell and took down primary and secondary P6 Dean St. ABB Order Id: 869916 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810098 | A
03/19/2026 07:21:01 | MECo | Bay State South | ABINGTON | PARK AVE | CENTRAL STREET UNIT 67 | 07-67J1 | 15 | OH | 7 | 0 | 25.86 | 180.95 | 02/23/2026 08:36 | 02/24/2026 10:28 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/23/2026 12:00 |  | N |  |  |  |  | Blown line fuses P26 Park Ave due to tree on primary P18 Park Ave -- needed town to plow road prior to tree removal. ABB Order Id: 873058 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8839231 | A
03/19/2026 07:13:49 | MECo | Bay State South | ABINGTON | CENTRE AVE | CENTRAL STREET UNIT 67 | 07-67J1 | 5 | OH | 6 | 0 | 5.36 | 32.10 | 02/23/2026 22:13 | 02/24/2026 03:35 | Failed Equipment | Transformer O/H conv. |  | BLIZ | M | N | Y | N | tc | 02/23/2026 22:13 |  | N |  |  |  |  | Initially commercial part power -- manually opened line fuses P36 Centre Ave to replace failed transformer bank P37 Centre Ave. Also replaced old pole. ABB Order Id: 873036 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810408 | A
03/18/2026 13:30:27 | MECo | Bay State South | WEYMOUTH | BRIDGE ST | NORTH WEYMOUTH 6 | 07-6W2 | 15 | OH | 6 | 0 | 5.00 | 30.00 | 02/24/2026 10:29 | 02/24/2026 15:29 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/24/2026 15:00 |  | N |  |  |  |  | Blown line fuses (2/3) P19 Bridge St. Cause: unknown. ABB Order Id: 873524 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810634 | A
03/18/2026 13:22:35 | NanECo | Bay State South | NANTUCKET | SOUTH PROSPECT ST | CANDLE STREET 101 | 04-101L4 | 5 |  | 26 | 0 | 52.86 | 1374.10 | 02/23/2026 08:13 | 02/25/2026 13:04 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/25/2026 12:00 |  | N |  |  |  |  | Blown transformer fuse P2 South Prospect St feeding West York.Ln. ABB Order Id: 872011 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811086 | A
03/18/2026 13:15:56 | NanECo | Bay State South | NANTUCKET | UNION ST | CANDLE STREET 101, CANDLE STREET 101 | 04-101L4, 04-101L7 | 15 | OH | 3415 | 0 | 74.68 | 15604.52 | 02/23/2026 09:16 | 02/26/2026 11:57 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 10:00 |  | N |  |  |  |  | Pole top recloser lockout P11 Union St, cause was tree fell between P8-9 West Dover St, crew knocked off. Blizzard 2026 Other scattered damage found while on patrol. Note: 101L4 was carrying about half of 101L7 due to a getaway fault yesterday. Note: customer counts are reduced by previous fuses blown and isolation switching (see other IDS events). ABB Order Id: 872010 Isolated at P9 Atlantic for wires down on Sparks Rd. ABB Order Id: 873544 ABB Order Id: 872888 Blown line fuse P3 Vesper Ln due to primary down P1 Gouin Village Rd. ABB Order Id: 871983 ABB Order Id: 871403 ABB Order Id: 872054 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811203 | A
03/18/2026 12:25:04 | NanECo | Bay State South | NANTUCKET | NOBADEER AVE | CANDLE STREET 101 | 04-101L7 | SY | OH | 46 | 0 | 20.59 | 946.83 | 02/24/2026 15:25 | 02/25/2026 12:00 | Failed Equipment | Overhead Device Other |  | NORM | M | N | Y | N | tc |  |  | N |  |  |  |  | Opened line fuse at P12 Nobadeer Ave for emergency repairs due to arcing wires. Blizzard 2026. ABB Order Id: 873793 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811137 | A
03/18/2026 12:24:12 | NanECo | Bay State South | NANTUCKET | UNION ST | CANDLE STREET 101, CANDLE STREET 101 | 04-101L4, 04-101L7 | 15 | OH | 2827 | 0 | 68.82 | 12023.33 | 02/23/2026 05:11 | 02/26/2026 02:00 | Physical Interference / Company | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 05:50 |  | N |  |  |  |  | Pole top recloser at P13 Surfside Rd (North) locked out due to a phase down at P5 Surfside Rd (South) while feeding portion of 101L7 (101L7 had a getaway failure yesterday). Opened loadbreak at P2 Surfside Rd (South) to isolate and closed PTR at P13 Surfside Rd to restore most customers. Ice covered conductors blown together in the wind. Blizzard 2026. Blown line fuse P9 Bartlett due to ice buildup P10 Cato Ln. Failed primary. Refused at 2100. ABB Order Id: 872111 ABB Order Id: 870158 Manually opened line fuse P33 Surfside Rd to make repairs for multiple trees and wires down. ABB Order Id: 873628 ABB Order ID: 873042 Broken ridge pins at poles 5 and 6 Grey Ave, caused line fuse to open at P3 Parker Ave. Replaced pins and closed line fuse to restore customers at 0200. ABB Order Id: 873044 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810908 | A
03/18/2026 12:09:41 | NanECo | Bay State South | NANTUCKET | OLD SOUTH RD | CANDLE STREET 101 | 04-101L7 | 5 |  | 21 | 0 | 75.00 | 1575.00 | 02/23/2026 10:24 | 02/26/2026 13:25 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/26/2026 12:30 |  | N |  |  |  |  | Blown transformer fuse P51 Old South Rd. Cause unknown. Blizzard 2026. ABB Order Id: 873033 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8838717 | A
03/17/2026 15:10:59 | MECo | Bay State South | WEYMOUTH | PILGRIM RD | NORTH WEYMOUTH 6 | 07-6W2 | 15 | OH | 97 | 0 | 20.82 | 2019.22 | 02/23/2026 03:49 | 02/24/2026 00:39 | Physical Interference / Company | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/23/2026 23:45 |  | N |  |  |  |  | Blown line fuses (2 of 3) P11 Pilgrim Rd. Suspected cause: phases slapping together in high wind. ABB Order ID: 869974, 869975 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8817022 | A
03/17/2026 14:41:06 | NanECo | Bay State South | NANTUCKET | EASY ST | CANDLE STREET 101 | 04-101L3 | 15 | OH | 1237 | 0 | 27.35 | 14557.73 | 02/23/2026 15:38 | 02/24/2026 19:00 | Unknown | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 18:00 |  | N |  |  |  |  | Phase down between P1 Center & P4 West Chester St (which goes to an open tie switch). Before this could be repaired, 2 phases came down at P5 South Beach Rd, causing pole top recloser lockout at P10 South Beach Rd. Further patrol found a need to open fuses at P10 Easton St. Manually opened 101L3 breaker at Candle St Sub to repair at P5 South Beach. Closed PTR at P10 South Beach Rd after isolating Easton St. ABB Order Id: 872592 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811243 | A
03/17/2026 14:12:42 | NanECo | Bay State South | NANTUCKET | NORTH BEACH ST | CANDLE STREET 101 | 04-101L3 | 15 | OH | 21 | 0 | 43.33 | 910.00 | 02/24/2026 11:12 | 02/26/2026 06:32 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/26/2026 06:00 |  | N |  |  |  |  | Blown line fuse P3 North Beach Rd. Cause unknown. Blizzard 2026. ABB Order ID: 873662 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8814943 | A
03/17/2026 14:12:26 | MECo | Bay State South | WEYMOUTH | NECK ST | NORTH WEYMOUTH 6 | 07-6W2 | 15 | OH | 679 | 0 | 6.97 | 4719.05 | 02/23/2026 08:32 | 02/23/2026 15:30 | Unknown | Overhead Device Other |  | WIND | M | Y | Y | N | tc | 02/23/2026 12:00 |  | N |  |  |  |  | Pole top recloser lockout P22-30 Neck St. Cause: 3 phases down at P36 River St from unknown cause. Outage number reduced due to existing outage event# 8810476. ABB Order Id: 871203 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810288 | A
03/17/2026 14:10:34 | MECo | Bay State South | WEYMOUTH | NECK ST | NORTH WEYMOUTH 6 | 07-6W2 | 15 | OH | 92 | 0 | 25.88 | 1584.47 | 02/23/2026 08:11 | 02/24/2026 10:04 | Failed Equipment | Tap |  | NORM | M | N | Y | N | tc | 02/24/2026 08:30 |  | N |  |  |  |  | Outage to customers on Regatta Rd. Cause: failed tap at P4 Regatta Rd at intersection of Great Hill at Regatta. Manually opened line fuse at P32 Neck St to make repairs. ABB Order Id: 873123, 872594 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810476 | A
03/17/2026 14:02:12 | NanECo | Bay State South | NANTUCKET | HINCKLEY LN | CANDLE STREET 101 | 04-101L3 | 15 | OH | 58 | 0 | 72.48 | 4204.03 | 02/23/2026 08:14 | 02/26/2026 08:43 | Unknown | Conductors |  | BLIZ | M | N | Y | N | tc | 02/26/2026 07:30 |  | N |  |  |  |  | Blown line fuse P1 Hinckley Ln. Wires down P5 Hinckley Ln. Cause unknown. Blizzard 2026. ABB Order ID: 874516, 872592 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8814717 | A
03/17/2026 13:50:10 | NanECo | Bay State South | NANTUCKET | CLIFF RD | CANDLE STREET 101 | 04-101L3 | 15 | OH | 138 | 0 | 58.95 | 7765.03 | 02/24/2026 04:03 | 02/26/2026 15:00 | Unknown | Conductors |  | BLIZ | M | N | Y | N | tc | 02/26/2026 11:00 |  | N |  |  |  |  | Blown line fuse P20 Cliff St. Wires down at P12 Lincoln St. Cause unknown. Blizzard 2026. ABB Order ID: 873572 ABB Order Id: 874586 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8814463 | A
03/17/2026 13:36:19 | NanECo | Bay State South | NANTUCKET | CLIFF RD | CANDLE STREET 101 | 04-101L3 | 15 | OH | 15 | 0 | 68.62 | 1029.25 | 02/23/2026 07:18 | 02/26/2026 03:55 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/26/2026 03:00 |  | N |  |  |  |  | Blown line fuse P27 Cliff St. Cause unknown. Blizzard 2026. ABB Order ID: 870820 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8814191 | A
03/17/2026 13:27:44 | NanECo | Bay State South | NANTUCKET | CLIFF RD | CANDLE STREET 101 | 04-101L3 | 15 | OH | 52 | 0 | 65.45 | 3403.40 | 02/23/2026 07:48 | 02/26/2026 01:15 | Unknown | Conductors |  | BLIZ | M | N | Y | N | tc | 02/26/2026 00:15 |  | N |  |  |  |  | Blown line fuse P16 Cliff St. Wire down on North Liberty St around P24. Blizzard 2026. Cause unknown. ABB Order Id: 870820, 873412 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8813915 | A
03/17/2026 11:40:31 | MECo | Bay State South | QUINCY | HANCOCK ST | ATLANTIC 4 | 07-4J3 | 5 | OH | 136 | 0 | 14.45 | 1844.60 | 02/23/2026 03:37 | 02/23/2026 18:05 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 04:30 |  | N |  |  |  |  | Blown line fuse (1 of 3) P28 Hancock St. Cause: phases slapping together on Hancock St. Shortly after refusing, different phase fuse at same location blew followed by original fuse blowing again. Field crews waited until wind subsided before refusing again. ABB Order ID: 869962, 870936, 870081, 870241, 870088 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810279 | A
03/17/2026 10:22:36 | NanECo | Bay State South | NANTUCKET | WASHINGTON ST | CANDLE STREET 101 | 04-101L2 | 15 | OH | 412 | 0 | 96.72 | 6556.98 | 02/23/2026 06:52 | 02/27/2026 07:35 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 14:00 |  | N |  |  |  |  | Pole top recloser at P10 Washington St locked out due to ice buildup on primary, swinging together in wind - wind blowing water from the ocean into the air and freezing on the wires. Blizzard 2026. ABB Order Id: 870684 Blown transformer fuse P43 Orange St cause was tree on wires. ABB Order Id: 873283 Broken tap on transformer cutout at P1 Meader St. Replaced cutout and restored customers. ABB Order Id: 874644 Repaired down secondaries at Pole 43 Orange St. ABB Order Id: 874627 Refused at P33 Orange St. ABB Order Id: 874626 ABB Order Id: 873284 Note: PTR at P10 Polpis Rd had previously locked out (se other IDS event) | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810912 | A
03/17/2026 10:16:35 | NanECo | Bay State South | NANTUCKET | WASHINGTON ST | CANDLE STREET 101 | 04-101L2 | 15 | OH | 44 | 0 | 7.89 | 346.87 | 02/23/2026 09:18 | 02/23/2026 17:11 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/23/2026 14:00 |  | N |  |  |  |  | 101L2 feeder lockout at Candle St Sub. Blizzard 2026. Note: pole top recloser at P10 Washington St was already locked out. Ice buildup on wires and strong winds blew phases together. Knocked ice off wires. ABB Order ID: 871422 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8813712 | A
03/17/2026 10:07:10 | NanECo | Bay State South | NANTUCKET | POLPIS RD | CANDLE STREET 101 | 04-101L2 | 15 | OH | 1155 | 0 | 98.02 | 32971.68 | 02/23/2026 06:25 | 02/27/2026 08:26 | Tree Contact | Switch Loadbreak |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 15:00 |  | N |  |  |  |  | Pole top recloser lockout at P10 Polpis Rd. Multiple issues found. Tree swaying into wires at P22 Polpis Rd. Failed loadbreak P96 Polpis Rd. Isolated sections, patrolled and restored as repairs were made. Blown line fuse P21 Sankaty Rd due to tree down line on Bayberry Sconset. Blizzard 2026. ABB Order Id: 873326 ABB Order ID: 870442 ABB Order Id: 873245 ABB Order Id: 872984 P57 Polpis Rd. Repaired primary and secondary at multiple locations. Refused (3) 40k fuses at p57 Polpis Rd ABB Order Id: 873248 Down wires caused line fuse to open at P122 Polpis Rd. Wires repaired, and line fuse replaced at 2050. ABB Order Id: 873246 Secondary brought down by ice, made repairs and put back up the secondary. Customers restored 2250 02/26 ABB Order Id: 874263 Repaired primary lines, cause unknown ABB Order Id: 874643 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810592 | A
03/17/2026 08:26:10 | MECo | Bay State South | QUINCY | SOUTHERN ST | FIELD STREET 1 | 07-1W1 | 15 | OH | 6 | 0 | 8.65 | 51.90 | 02/24/2026 05:33 | 02/24/2026 14:12 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/24/2026 13:50 |  | N |  |  |  |  | Blown riser fuses (2 of 3) at P103 Washington St. Cause: unknown. ABB Order Id: 873254 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810587 | A
03/17/2026 08:18:25 | MECo | Bay State South | QUINCY | WASHINGTON ST | FIELD STREET 1 | 07-1W1 | SY | OH | 2 | 0 | 29.57 | 59.13 | 02/23/2026 06:26 | 02/24/2026 12:00 | Unknown | Connector |  | WIND | M | N | Y | N | tc | 02/24/2026 08:50 |  | N |  |  |  |  | No power to addresses 13 and 15 Kittredge Ave. Cause: service pulled off building (duplex) due to unknown cause and was cut clear for safety. Overhead crew ran new service. ABB Order Id: 870464 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810515 | A
03/17/2026 07:57:26 | MECo | Bay State South | QUINCY | CHUBBUCK ST | FIELD STREET 1 | 07-1W1 | 15 | OH | 783 | 0 | 9.94 | 7777.80 | 02/23/2026 04:31 | 02/23/2026 14:28 | Failed Equipment | Splice |  | WIND | M | Y | Y | N | tc | 02/23/2026 04:54 |  | N |  |  |  |  | Pole top recloser trip and reclose P47 Washington St and sectionalizing PTR opened on undervoltage at P3-50 Chubbuck St. Cause: splice failed and caused wire down at P27 East Howard St. Restoration was delayed due to high wind. ABB Order Id: 870023 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810191 | A
03/16/2026 15:24:22 | MECo | Bay State North | GLOUCESTER | EAST MAIN ST | GLOUCESTER 24 | 12-24J9 | 5 | OH | 16 | 0 | 27.90 | 446.13 | 02/23/2026 06:36 | 02/24/2026 10:30 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 10:10 |  | N |  |  |  |  | Blown line fuses (2 of 2) P2674 East Main St cause unknown. ABB Order Id: 870546 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810487 | A
03/16/2026 15:21:27 | MECo | Bay State North | GLOUCESTER | CHAPEL ST | GLOUCESTER 24 | 12-24J9 | 5 | OH | 30 | 0 | 30.45 | 913.00 | 02/23/2026 04:48 | 02/24/2026 11:15 | Physical Interference / Company | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/24/2026 10:00 |  | N |  |  |  |  | Blown A and B phase line fuses (2 of 3) P2659 Chapel St caused by phases slapping P2663 Chapel St during winter weather event. ABB Order Id: 870035, 873333, 870848 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810503 | A
03/16/2026 15:05:18 | MECo | Bay State North | GLOUCESTER | RAILROAD AVE | GLOUCESTER 24 | 12-24J8 | 5 | OH | 18 | 0 | 34.95 | 629.10 | 02/23/2026 05:27 | 02/24/2026 16:25 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/24/2026 15:45 |  | N |  |  |  |  | Blown line fuses (2 of 3) P3591 Railroad Ave, cause unknown. ABB Order Id: 872530 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810680 | A
03/16/2026 15:00:12 | MECo | Bay State North | GLOUCESTER | ROGERS ST | GLOUCESTER 24 | 12-24J7 | 5 | OH | 7 | 0 | 52.78 | 369.37 | 02/23/2026 11:15 | 02/25/2026 16:01 | Unknown | Conductors |  | WIND | M | Y | Y | N | tc | 02/23/2026 11:30 |  | N |  |  |  |  | 2 of 3 phases to mainline tapped P7953 Rogers St came down during winter weather event, no cause found. ABB Order Id: 873375 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811069 | A
03/16/2026 14:34:39 | MECo | Bay State North | GLOUCESTER | BASS AVE | GLOUCESTER 24 | 12-24J2 | 5 | OH | 27 | 0 | 26.65 | 719.10 | 02/23/2026 11:21 | 02/24/2026 14:00 | Failed Equipment | Tap |  | WIND | M | N | Y | N | tc | 02/24/2026 12:00 |  | N |  |  |  |  | 24J2 Circuit Breaker tripped and reclosed at Gloucester Substation caused by failed high side tap to line fuse cutout P870 Bass Ave. ABB Order Id: 872897 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810603 | A
03/11/2026 22:35:49 | MECo | Bay State North | GLOUCESTER | WILEY ST | GLOUCESTER 24 | 12-24J10 | SY | OH | 1 | 0 | 17.08 | 17.07 | 02/24/2026 16:25 | 02/25/2026 09:30 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/25/2026 08:00 |  | N |  |  |  |  | Tree took down service drop to house 11 Wiley St. ABB Order Id: 873794 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810979 | A
03/11/2026 22:33:32 | MECo | Bay State North | GLOUCESTER | ROCKY NECK AVE | GLOUCESTER 24 | 12-24J10 | 5 | OH | 235 | 0 | 29.70 | 5854.30 | 02/23/2026 05:12 | 02/24/2026 10:54 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 00:15 |  | N |  |  |  |  | Blown line fuses P1646 Rocky Neck Ave caused by tree that took down primary and secondary P2627 Rocky Neck Ave. Crews isolated opening line fuses P2971 Rocky Neck Ave and closing P1646 Rocky Neck while making repairs. ABB Order Id: 872460, 873197 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810379 | A
03/11/2026 22:10:33 | MECo | Bay State North | GLOUCESTER | ST LOUIS AVE | GLOUCESTER 24 | 12-24J10 | 5 | OH | 91 | 0 | 54.24 | 3400.28 | 02/23/2026 07:57 | 02/25/2026 14:12 | Tree Contact | Conductors |  | WIND | M | Y | Y | N | tc | 02/23/2026 14:00 |  | N |  |  |  |  | Blown line fuses P7387 St Louis Ave caused by tree taking down primary and secondary P7771 Fort Hill Ave. Riser fuse was found open P2689 Eastern Point with no cause found, so those customers remained out until underground crew tested cable okay. ABB Order Id: 872576, 872970, 874009 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810789 | A
03/11/2026 19:48:50 | MECo | Bay State North | GLOUCESTER | RIGGS ST | GLOUCESTER 24 | 12-24J1 | 5 | OH | 6 | 0 | 79.38 | 476.30 | 02/23/2026 04:52 | 02/26/2026 12:15 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/26/2026 10:00 |  | N |  |  |  |  | Blown B phase line fuse (1 of 3) P2875 Riggs St. Cause unknown. ABB Order Id: 873974 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8812178 | A
03/11/2026 19:06:14 | MECo | Bay State North | MANCHESTER | UNION ST | MANCHESTER 23 | 12-23H2 | SY |  | 56 | 0 | 1.56 | 86.80 | 02/24/2026 19:59 | 02/24/2026 21:33 | Failed Equipment | Cable - Other |  | NORM | M | N | Y | N | tc | 02/24/2026 19:59 |  | N |  |  |  |  | Manually disconnected submersible transformer MH86 Union to de-energize make repairs to secondary issues. No customers had outage until crews disconnected XFR. ABB Order Id: 873994 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810844 | A
03/11/2026 18:57:44 | MECo | Bay State North | MANCHESTER | FOREST ST | MANCHESTER 23 | 12-23H2 | 5 | OH | 3 | 0 | 27.94 | 83.80 | 02/23/2026 10:56 | 02/24/2026 14:53 | Tree Contact | Pole - wood |  | WIND | M | N | Y | N | tc | 02/24/2026 07:00 |  | N |  |  |  |  | Blown line fuse P25 Forest St caused by tree falling and breaking 3 poles and taking primary down P27 - P30 Mill St. ABB Order Id: 871970 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810609 | A
03/11/2026 18:51:25 | MECo | Bay State North | MANCHESTER | SUMMER ST | MANCHESTER 23 | 12-23H1 | 5 | UG | 13 | 0 | 15.59 | 202.58 | 02/24/2026 14:46 | 02/25/2026 06:21 | Failed Equipment | Cable - XLPE - PE |  | NORM | M | N | Y | N | tc | 02/24/2026 16:00 |  | N |  |  |  |  | Blown -3 fuses at SWGR 12 Summer St caused by primary cable fault MH33 Beach at Summer. ABB Order Id: 873731 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810940 | A
03/11/2026 05:23:47 | MECo | Bay State North | REVERE | WALNUT AVE | REVERE 7 | 12-7J6 | 5 | OH | 78 | 0 | 16.13 | 1257.10 | 02/23/2026 09:23 | 02/24/2026 01:31 | Unknown | No failure or Unknown |  | OTHR | M | Y | Y | N | tc | 02/24/2026 00:30 |  | N |  |  |  |  | Blown A and C phase line fuses (2 of 3) P675 Walnut Ave with no cause found. Overrode customer count to accurately reflect 2 of 3 phase residential customers affected. ABB Order Id: 872828, 871784, 871501 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810441 | A
03/11/2026 05:11:45 | MECo | Bay State North | REVERE | NORTH SHORE RD | REVERE 7 | 12-7J3 | 5 | OH | 40 | 0 | 16.64 | 665.33 | 02/23/2026 05:07 | 02/23/2026 21:46 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 21:00 |  | N |  |  |  |  | Blown B and C phase line fuses (2 of 3) P1490 North Shore Rd, suspected phase slap during winter weather event but no cause found. ABB Order Id: 871742, 870143, 870137 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810338 | A
03/10/2026 21:12:14 | MECo | Bay State North | EVERETT | BEACHAM ST | HENDERSONVILLE 593 | 12-593W1 | 15 | OH | 1 | 0 | 11.41 | 11.40 | 02/23/2026 11:23 | 02/23/2026 22:48 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 22:00 |  | N |  |  |  |  | Blown line fuse P3028 Beacham St caused by tree branches being blown into primary P3028-2 Beacham during winter weather event. Crew rubbered up primary and refused. ABB Order Id: 872031 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810361 | A
03/10/2026 21:02:23 | MECo | Bay State North | REVERE | TUTTLE ST | REVERE BEACH 35 | 12-35J4 | 5 | OH | 19 | 0 | 41.56 | 789.45 | 02/23/2026 07:26 | 02/25/2026 01:00 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 23:00 |  | N |  |  |  |  | Tree took down service wire to house 35 Tuttle St. ABB Order Id: 870861, 873516 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8812104 | A
03/10/2026 20:58:15 | MECo | Bay State North | LYNN | TRACY AVE | MELROSE 4 | 12-4J2 | 5 | OH | 1 | 0 | 20.85 | 20.83 | 02/23/2026 06:11 | 02/24/2026 03:02 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 02:00 |  | N |  |  |  |  | Tree limb took down service to house 174 Tracy Ave. Customer will need electrician and MUNI prior to NGrid running new service. ABB Order Id: 870383 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810399 | A
03/10/2026 20:43:32 | MECo | Bay State North | REVERE | HUTCHINSON ST | REVERE BEACH 35 | 12-35J1 | 5 | OH | 31 | 0 | 15.53 | 481.02 | 02/23/2026 05:22 | 02/23/2026 20:54 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 20:00 |  | N |  |  |  |  | Blown line fuses (2 of 3) P2663 Hutchinson St. No cause. ABB Order Id: 870202 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810319 | A
03/10/2026 20:15:28 | MECo | Bay State North | LYNN | BICKFORD ST | WEST SALEM 29 | 12-29W4 | 15 |  | 4 | 0 | 2.30 | 9.20 | 02/23/2026 05:11 | 02/23/2026 07:30 | Failed Equipment | Tap |  | WIND | M | N | Y | N | tc | 02/23/2026 06:30 |  | N |  |  |  |  | Failed transformer tap P49 Bickford St. ABB Order Id: 870159 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810259 | A
03/10/2026 18:57:47 | MECo | Bay State North | BEVERLY | ODELL AVE | EAST BEVERLY 51 | 12-51L2 | 5 | OH | 12 | 0 | 31.26 | 375.00 | 02/23/2026 07:59 | 02/24/2026 15:15 | Tree Contact | Conductors |  | OTHR | M | Y | Y | N | tc | 02/24/2026 12:00 |  | N |  |  |  |  | Tree took down service to house 41 ODell Ave. ABB Order Id: 871800 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811818 | A
03/10/2026 18:54:39 | MECo | Bay State North | BEVERLY | DODGE ST | EAST BEVERLY 51 | 12-51L1 | 15 | OH | 12 | 0 | 29.80 | 357.60 | 02/23/2026 07:41 | 02/24/2026 13:30 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 10:00 |  | N |  |  |  |  | Blown line fuse P1009 Dodge St caused by tree taking down primary P2 Beaver Pond Rd. ABB Order Id: 872182 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811819 | A
03/10/2026 18:28:45 | MECo | Bay State North | HAMILTON | BAY RD | EAST BEVERLY 51 | 12-51L3 | 15 | OH | 17 | 0 | 12.02 | 204.28 | 02/23/2026 04:19 | 02/23/2026 16:21 | Tree Contact | Overhead Device Other |  | WIND | M | N | Y | N | tc | 02/23/2026 15:00 |  | N |  |  |  |  | Blown line fuse P1461 Bay Rd caused by tree that took primary off the pin P1653 Carriage Ln. ABB Order Id: 870002 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810291 | A
03/10/2026 18:16:52 | MECo | Bay State North | HAMILTON | ASBURY ST | EAST BEVERLY 51 | 12-51L3 | SY | OH | 91 | 0 | 1.58 | 144.08 | 02/24/2026 08:50 | 02/24/2026 10:25 | Tree Contact | Overhead Device Other |  | WIND | M | Y | Y | N | tc | 02/24/2026 08:50 |  | N |  |  |  |  | Crews manually opened stepdown transformer fuses P638, P1140, and P1141 Asbury to remove tree and hang primary back on pins P1081 to P1084 Asbury St. 4725362 ABB Order Id: 873420, 873421, 873419 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810622 | A
03/08/2026 08:36:45 | MECo | Bay State South | STOUGHTON | ISLAND ST | STOUGHTON | 07-913W69 | 15 | UG | 5 | 0 | 14.48 | 72.33 | 02/24/2026 10:44 | 02/25/2026 01:13 | Physical Interference / Other | Transformer padmount |  | BLIZ | M | N | Y | N | tc | 02/24/2026 21:00 |  | N |  |  |  |  | Blown line fuse P25 Island St. Minipad transformer knocked off foundation. Replaced transformer. Blizzard. ABB Order Id: 873648 ABB Order Id: 873532 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810878 | A
03/08/2026 08:30:49 | MECo | Bay State South | STOUGHTON | R.O.W. 1 X X | STOUGHTON | 07-913W69 | 15 | OH | 3563 | 0 | 30.37 | 48630.00 | 02/23/2026 05:52 | 02/24/2026 12:15 | Unknown | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 19:00 |  | N |  |  |  |  | 913W69 feeder trip and reclose at Stoughton Sub. Pole top recloser locked out at P72 Central St. No cause found on patrol past P72 Central, but a broken spacer cable phase was found at P48 Canton St (likely from fault current). Isolated by opening loadbreak P56 Canton St, and picking up remainder of feeder on ties to 913W18 and 913W43. At this point, the only customers still out of service (36) were on a C phase tap to Pratt St. When crews were available, manually opened 913W69 breaker at Stoughton Sub, fixed the broken phase, and closed breaker, restoring the remaining customers. Blizzard 2026. ABB Order Id: 870297 ABB Order Id: 873571 Also found blown line fuse P3 Elm St, looks like plow bumped pole opening the fuse, 6T. ABB Order Id: 873064 ABB Order Id: 872845 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810358 | A
03/08/2026 06:48:42 | MECo | Bay State South | BROCKTON | COURT ST | DUPONT SUB | 07-91W40 | 15 | OH | 373 | 0 | 35.68 | 8184.58 | 02/23/2026 07:15 | 02/24/2026 18:56 | Failed Equipment | Pole - wood |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 08:45 |  | N |  |  |  |  | Pole broken and C phase broken at P38 Court St. Pole deteriorated at base, blizzard conditions. Manually opened disconnects P44 Court St to make repairs. ABB Order Id: 871324 Pole 6 Freight St, blown 25T line fuses. ABB Order Id: 873586 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810474 | A
03/08/2026 06:31:50 | MECo | Bay State South | WHITMAN | TEMPLE ST | TEMPLE ST. UNIT 12 | 07-712J1 | 5 | OH | 1039 | 0 | 16.26 | 16883.75 | 02/23/2026 07:34 | 02/23/2026 23:49 | Unknown | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 21:00 |  | N |  |  |  |  | 712J1 feeder lockout at Temple St Sub. Patrolled, no cause found. Blizzard 2026. ABB Order Id: 870955 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810571 | A
03/07/2026 19:01:59 | MECo | Bay State South | ATTLEBORO | A P 22KV 2274 LINE LINE | ANP BLACKSTONE | 05-2274 | 15 | OH | 4 | 0 | 29.79 | 100.20 | 02/23/2026 05:03 | 02/24/2026 10:51 | Tree Contact | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/23/2026 06:22 |  | N |  |  |  |  | 2274 line lockout between West St Sub and Plainville Sub. Cause was tree down at P29 off Commonwealth Ave, North Attleboro. Customers picked up with feeder ties. ABB Order Id: 870121 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810640 | A
03/07/2026 15:10:14 | MECo | Bay State North | BEVERLY | GROVER ST | NORTH BEVERLY 18, EAST BEVERLY 51 | 12-18L2, 12-51L3 | 15 | OH | 2169 | 0 | 33.36 | 22008.85 | 02/23/2026 05:08 | 02/24/2026 14:30 | Tree Contact | Conductors |  | OTHR | M | Y | Y | N | tc | 02/23/2026 12:00 |  | N |  |  |  |  | 51L3 Circuit Breaker tripped and reclosed at E Beverly substation caused by a tree that parted B and C phase primary P480 Dodges ROW. Pole Top Recloser P501 Walnut Rd opened on loss of source but FLISR had previously operated and the 51L3 was carrying a portion of the 18L2 from P5 Bay Rd up to P345 Main St in Wenham. Opened P1595 Grover St to de-energized damage. Once 18L2 source became available, closed P345 Main up to P5 Bay Rd restoring all 18L2 customers. Patrolled OH and closed P5 Bay up to P501 Walnut. Opened P231 Dodges ROW to isolate back side of damage and backfed from P501 Walnut. Crews took tags to make repairs then closed P1595 Grover St for final mainline restore. Multiple side taps had been opened during overhead patrol and were restored one at a time after mainline. Customer count reduced due to previously existing outage (8810291) ABB Order Id: 871429 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810293 | A
03/07/2026 13:31:11 | MECo | Bay State North | BEVERLY | SYLVESTER AVE | BEVERLY 12 | 12-12L2 | 5 | OH | 1 | 0 | 19.45 | 19.43 | 02/23/2026 11:23 | 02/24/2026 06:50 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 05:45 |  | N |  |  |  |  | Tree broke service to house 2 Sylvester Ave. ABB Order Id: 872030 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810430 | A
03/07/2026 13:29:24 | MECo | Bay State North | BEVERLY | MCKAY ST | BEVERLY 12 | 12-12L2 | 15 | OH | 1 | 0 | 13.36 | 13.35 | 02/24/2026 14:08 | 02/25/2026 03:29 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 18:00 |  | N |  |  |  |  | Blown line fuses (2 of 3) P540 McKay St caused by branch breaking primary one pole away P4434 McKay. ABB Order Id: 873710 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810900 | A
03/07/2026 13:23:52 | MECo | Bay State North | REVERE | TOMASELLO RD | REVERE 7 | 12-7W4 | 15 | OH | 4 | 0 | 27.14 | 108.53 | 02/23/2026 08:03 | 02/24/2026 11:11 | Physical Interference / Company | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/24/2026 10:00 |  | N |  |  |  |  | Blown line fuses (2 of 3) P4 Tomasello Dr caused by phase slap P6 Tomasello. GIS drawn incorrectly, only customers out were Pad 2 Tomasello and Pad 1 Furlong. ABB Order Id: 871053, 873334 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810497 | A
03/07/2026 13:15:49 | MECo | Bay State North | BEVERLY | ENON ST | NORTH BEVERLY 18 | 12-18L2 | 5 | OH | 14 | 0 | 1.68 | 23.33 | 02/24/2026 11:24 | 02/24/2026 13:05 | Failed Equipment | Conductors |  | SNOW | M | N | Y | N | tc | 02/24/2026 12:00 |  | N |  |  |  |  | Crews replaced service to house 8 Enon St. ABB Order Id: 873573 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811812 | A
03/07/2026 13:12:22 | MECo | Bay State North | WENHAM | FRIEND CT | NORTH BEVERLY 18 | 12-18L2 | 5 | OH | 1 | 0 | 20.35 | 20.35 | 02/23/2026 21:58 | 02/24/2026 18:20 | Failed Equipment | Conductors |  | SNOW | M | N | Y | N | tc | 02/24/2026 17:00 |  | N |  |  |  |  | Failed service to house 25 Friend Ct. ABB Order Id: 873015 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810759 | A
03/07/2026 13:06:10 | MECo | Bay State North | BEVERLY | DODGE ST | NORTH BEVERLY 18 | 12-18L2 | SY |  | 747 | 0 | 6.55 | 4879.02 | 02/23/2026 04:51 | 02/23/2026 11:24 | Tree Contact | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 06:00 |  | N |  |  |  |  | 2362 Circuit Breaker locked out at N Beverly Substation caused by tree limb across primary P193 Topsfield Rd in the 2365 back up ROW to Topsfield sub from N Beverly. 2365 did not operate due to coordination issue that has since been resolved by Relay/DPAM settings change. This overtrip caused a loss of supply to 18L2 customers and the 4kV 2TR at N Beverly. 4kV bus transferred to the 2318 supply restoring 18J2 and 18J4 customers under 1 minute. 18L2 FLISR operated restoring customers from P345 Main via P5 Bay Rd. O&M opened 2365 CB, then closed 2362 supply CB and closed 18L2 restoring remaining customers. ABB Order Id: 870071,872240 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810317 | A
03/07/2026 12:06:40 | MECo | Bay State North | MELROSE | UPHAM ST | MELROSE 25 | 12-25W5 | 5 |  | 15 | 0 | 7.19 | 107.75 | 02/23/2026 11:19 | 02/23/2026 18:30 | Tree Contact | Pole - wood |  | WIND | M | N | Y | N | tc | 02/23/2026 11:19 |  | N |  |  |  |  | Crews opened transformer fuse P1849 Upham St to remove tree from secondary and replace broken P2481 Brookledge Rd. ABB Order Id: 870621, 872022 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810298 | A
03/07/2026 12:00:42 | MECo | Bay State North | MELROSE | PENNY RD | MELROSE 25 | 12-25W5 | 5 | OH | 19 | 0 | 11.22 | 213.12 | 02/23/2026 06:47 | 02/23/2026 18:00 | Unknown | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/23/2026 17:00 |  | N |  |  |  |  | Blown line fuse P2385 Penny Hill Rd during winter weather event with no cause found. ABB Order Id: 872566, 872805, 870598 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810262 | A
03/07/2026 11:35:54 | MECo | Bay State North | WENHAM | MAIN DR | NORTH BEVERLY 18 | 12-18L1 | 5 | OH | 28 | 0 | 31.32 | 697.77 | 02/23/2026 09:48 | 02/24/2026 17:07 | Tree Contact | Conductors |  | WIND | M | Y | Y | N | tc | 02/24/2026 08:30 |  | N |  |  |  |  | Tree took down primary and secondary and also damaged riser P1265 Main Dr. Crews opened high side step down transformer fuse P1261 Main Dr to make repairs. (There were no additional customers between failed primary and step down) Isolated P1265 and restored all customers except 5 Main Dr who was out until crews repaired riser. ABB Order Id: 871565, 873706, 873941 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810501 | A
03/07/2026 11:24:13 | MECo | Bay State North | WENHAM | TOPSFIELD RD | NORTH BEVERLY 18 | 12-18L1 | 15 | OH | 9 | 0 | 35.72 | 321.45 | 02/23/2026 05:31 | 02/24/2026 17:14 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 15:45 |  | N |  |  |  |  | Blown line fuse P18 Topsfield Rd caused by tree that damaged primary P993 Cedar St. ABB Order Id: 873661, 870235 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810712 | A
03/07/2026 11:04:18 | MECo | Bay State North | MELROSE | WYOMING AVE ST | MELROSE 25 | 12-25W4 | 15 | OH | 58 | 0 | 6.09 | 352.83 | 02/23/2026 06:29 | 02/23/2026 12:35 | Tree Contact | Cutout - open |  | SNOW | M | N | Y | N | tc | 02/23/2026 11:00 |  | N |  |  |  |  | Blown line fuse P2590 Wyoming Ave caused by tree limb falling and damaging transformer cutout P832 Lynde Ave. ABB Order Id: 870521 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810260 | A
03/07/2026 10:53:23 | MECo | Bay State North | SAUGUS | BROADWAY #2 ST | MELROSE 25 | 12-25W3 | 15 | OH | 2 | 0 | 35.88 | 71.73 | 02/23/2026 10:52 | 02/24/2026 22:45 | Physical Interference / Company | Conductors |  | OTHR | M | N | Y | N | tc | 02/24/2026 14:00 |  | N |  |  |  |  | Blown line fuses P188 Broadway caused by phase slap during blizzard that parted primary. ABB Order Id: 871951 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810850 | A
03/07/2026 10:46:53 | MECo | Bay State North | SAUGUS | BROADWAY #2 ST | MELROSE 25 | 12-25W3 | 15 | OH | 2 | 0 | 30.49 | 60.97 | 02/23/2026 10:13 | 02/24/2026 16:42 | Physical Interference / Company | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/24/2026 16:00 |  | N |  |  |  |  | Blown line fuse P194 Broadway caused by phases slap during blizzard. ABB Order Id: 871785 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810692 | A
03/07/2026 10:42:31 | MECo | Bay State South | STOUGHTON | MAPLE ST |  | 07-75W7 | 15 | OH | 1 | 0 | 28.27 | 28.27 | 02/23/2026 09:08 | 02/24/2026 13:25 | Physical Interference / Company | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 12:30 |  | N |  |  |  |  | Blown 2 of 3 line fuses at P11 Maple St 25T. Phase slap in the wind. ABB Order Id: 873198 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810586 | A
03/07/2026 10:32:59 | MECo | Bay State South | AVON | HARRISON BLVD |  | 07-75W3 | 15 | OH | 347 | 0 | 26.86 | 7945.05 | 02/23/2026 12:52 | 02/24/2026 15:43 | Tree Contact | Network Protector |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 07:26 |  | N |  |  |  |  | Pole top recloser lockout at P53--3 R/W off West Main St. P1-1 Ladge Dr, tree limb on wires (radial tap). Blizzard. FLISR operated properly, transferring customers past P42 West Main St to 911W59. ABB Order Id: 872289 Blown transformer fuse P5 Victory Ave - repaired broken neutral on secondary and refused secondary tub ABB Order Id: 873593 ABB Order Id: 873608 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810511 | A
03/07/2026 10:29:54 | MECo | Bay State North | SAUGUS | BEECH ST | MANCHESTER 23 | 12-23W1 | 5 | OH | 1 | 0 | 38.18 | 38.18 | 02/23/2026 10:49 | 02/25/2026 01:00 | Failed Equipment | Conductors |  | SNOW | M | N | Y | N | tc | 02/24/2026 23:30 |  | N |  |  |  |  | Failed service to house 25 Beech St. ABB Order Id: 872765 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810274 | A
03/07/2026 10:25:32 | MECo | Bay State South | AVON | GLENDOWER ST |  | 07-75W3 | SY | OH | 1 | 0 | 13.87 | 13.87 | 02/24/2026 10:34 | 02/25/2026 00:26 | Failed Equipment | Connector |  | BLIZ | M | N | Y | N | tc | 02/24/2026 23:30 |  | N |  |  |  |  | 39 Glendower St, service drop pulled off building. Customer also needs electrician. ABB Order Id: 873526 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810872 | A
03/07/2026 10:15:41 | MECo | Bay State North | LYNN | LYNNWAY ST | LYNN 21 | 12-21J27 | 5 | OH | 1 | 0 | 31.33 | 31.32 | 02/23/2026 06:22 | 02/24/2026 13:42 | Failed Equipment | Conductors |  | SNOW | M | N | Y | N | tc | 02/24/2026 13:00 |  | N |  |  |  |  | Crews replaced service to house 525 Lynnway. ABB Order Id: 870428 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810560 | A
03/07/2026 10:10:38 | MECo | Bay State North | SWAMPSCOTT | GREENWOOD AVE | SALEM 1 PEABODY ST | 12-1J903 | 5 | OH | 1 | 0 | 20.44 | 20.43 | 02/23/2026 06:29 | 02/24/2026 02:55 | Failed Equipment | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 02:00 |  | N |  |  |  |  | Failed service to house 402 Humphrey St. ABB Order Id: 870510 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810400 | A
03/07/2026 10:08:52 | MECo | Bay State North | SWAMPSCOTT | HUMPHREY ST | SALEM 1 PEABODY ST | 12-1J902 | SY | OH | 1 | 0 | 22.92 | 22.92 | 02/23/2026 06:57 | 02/24/2026 05:52 | Adverse Environment | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 05:00 |  | N |  |  |  |  | Failed service to house 12 Blaney St. ABB Order Id: 870718 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810416 | A
03/07/2026 09:57:43 | MECo | Bay State North | LYNNFIELD |  | TURNPIKE 19 | 12-19W2 | 15 | OH | 608 | 0 | 17.08 | 7314.57 | 02/23/2026 04:47 | 02/23/2026 21:52 | Failed Equipment | Crossarm |  | WIND | M | Y | Y | N | tc | 02/23/2026 15:00 |  | Y | Brendan O Regan;Scott Crabtree;, Brendan O Regan;Scott Crabtree; | Email (boregan@saugus-ma.gov);Email (scrabtree@saugus-ma.gov);, Email (boregan@saugus-ma.gov);Email (scrabtree@saugus-ma.gov); |  |  | 19W2 Circuit Breaker locked out at Turnpike Substation with no initial cause found on patrol. Closed CB which held for a few minutes then tripped and reclosed, then locked out 20 minutes later. Subsequent patrol found 2 of 3 line fuse blown P65 Broadway at the Salvation Army caused by failed crossarm and burnt insulators. Opened remaining fuse to isolate. P123 Broadway also had failed dead end bell that crews isolated and repaired after mainline was re-energized. ABB Order Id: 870060, 871674 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810360 | A
03/07/2026 09:46:45 | MECo | Bay State South | BROCKTON | R.O.W. 14 X X | AMES SUB | 07-911W77 | 15 | OH | 2658 | 0 | 19.15 | 16669.68 | 02/23/2026 09:29 | 02/24/2026 04:38 | Tree Contact | Crossarm |  | BLIZ | M | Y | Y | N | tc | 02/24/2026 01:00 |  | N |  |  |  |  | 911W77 feeder lockout at Ames St Sub. Tree down at P48 East Ashland St, Brockton - also single phase lateral to Upton St., Brockton. Replaced offset arm and insulator and 10 feet of 4/0 wire on Upton St. Blizzard. FLISR operated properly, restoring all customers past P71 East Ashland St onto 97W3. ABB Order Id: 871482 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810491 | A
03/07/2026 09:13:04 | MECo | Bay State North | SAUGUS | EDISON ST | TURNPIKE 19 | 12-19W1 | SY | OH | 1 | 0 | 10.32 | 10.32 | 02/23/2026 10:41 | 02/23/2026 21:00 | Tree Contact | Conductors |  | NORM | M | N | Y | N | tc | 02/23/2026 19:00 |  | N |  |  |  |  | Tree fell and took down service and customer owned equipment at 33 Fairmount Ave. Cut power at pole. Customer needs an electrician and inspection prior to reconnect. ABB Order Id: 873953, 871921 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810884 | A
03/07/2026 09:07:38 | MECo | Bay State North | MEDFORD | WARREN ST | WEST MEDFORD 17 | 12-17J3 | 15 |  | 11 | 0 | 7.70 | 84.70 | 02/23/2026 10:07 | 02/23/2026 17:50 | Failed Equipment | Cutout door/fuse holder |  | SNOW | M | N | Y | N | tc | 02/23/2026 17:15 |  | N |  |  |  |  | Blown transformer fuse P949 Warren St caused by failed cutout door. ABB Order Id: 871741 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810252 | A
03/07/2026 07:47:01 | MECo | Bay State South | ROCKLAND | FOREST ST | NORTH ABINGTON SUB | 07-99W63 | 15 | OH | 275 | 0 | 25.12 | 6907.08 | 02/23/2026 04:02 | 02/24/2026 05:09 | Unknown | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/24/2026 03:00 |  | N |  |  |  |  | Blown line fuses P23 Forest St, cause unknown, windy blizzard conditions. ABB Order Id: 873113 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811787 | A
03/07/2026 07:10:34 | MECo | Bay State South | NORWELL | 33 LINE ROW ROW | NORWELL SUB | 07-96W44 | 15 | OH | 337 | 0 | 35.84 | 3934.17 | 02/23/2026 09:05 | 02/24/2026 20:56 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 16:00 |  | N |  |  |  |  | 96W44 feeder lockout at Norwell Sub. Tree found across all 3 phases in R/W P182 R/W between South and Main St. Note: Pole top recloser at P253 Main St was already locked out when the feeder breaker tripped (see other IDS event). ABB Order Id: 873622 ABB Order Id: 871363 ABB Order Id: 872937 ABB Order Id: 872920 ABB Order Id: 872934 ABB Order Id: 872938 ABB Order Id: 872968 ABB Order Id: 872916 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810303 | A
03/07/2026 06:19:29 | MECo | Bay State South | NORWELL | MAIN ST | NORWELL SUB | 07-96W44 | 15 | OH | 1255 | 0 | 38.44 | 18816.72 | 02/23/2026 08:14 | 02/24/2026 22:40 | Tree Contact | Conductors |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 16:00 |  | Y | Tim Kane;Jason Cavallaro; | Email (Timothy.kane@hanover-ma.gov);Email (jason.cavallaro@hanover-ma.gov); |  |  | Pole top recloser lockout P253 Main St AB targets. Only damage found on patrol was fallen tree with wires down P2-P3 Oak St. Manually opened line fuses P64 Washington St and closed tie PTR P173 Webster St to backfeed (could not get P253 to close) ABB Order Id: 871118 Blown 2 of 3 line fuses P176 Webster St. Phases must have slapped together. ABB Order Id: 873668 ABB Order Id: 872924 Fuse blown at P251, corner of Main St & Bowker. Refused 100T at Pole 251. Casue was a phase off the insulator at Pole 15. ABB Order Id: 872909 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811066 | A
03/06/2026 16:38:28 | MECo | Bay State North | REVERE | CHARGER ST | MAPLEWOOD 16 | 12-16W4 | SY | OH | 13 | 0 | 10.12 | 41.43 | 02/25/2026 10:50 | 02/25/2026 20:57 | Physical Interference / Other | Pole - wood |  | SNOW | M | Y | Y | N | tc | 02/25/2026 10:50 |  | N |  |  |  |  | MVA broke P5154-9 and P5154-10 on Charger St. Manually opened 3 fuses P5154 Charger St to de-energize for entrapment from the MVA. Crews made an airgap at P5154-8 Charger and closed fuses P5154 Charging restoring some customers prior to making repairs. Opened fuses P5154 Charger once repairs were completed to close airgap de-energized, restoring all customers. ABB Order Id: 874223, 874273, 874446 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811020 | A
03/06/2026 16:26:06 | MECo | Bay State North | MALDEN | COLEMAN ST | MAPLEWOOD 16 | 12-16W4 | 15 | OH | 2510 | 0 | 0.03 | 41.83 | 02/23/2026 19:25 | 02/23/2026 19:26 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 19:26 |  | N |  |  |  |  | 16W4 Circuit Breaker tripped and did not attempt to reclose at Maplewood Substation. SCADA closed CB and later patrol found no cause. O&M to investigate reclosing timer. | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811756 | A
03/06/2026 16:25:14 | MECo | Bay State North | MALDEN | COLEMAN ST | MAPLEWOOD 16 | 12-16W4 | 15 | OH | 2510 | 0 | 0.04 | 83.67 | 02/23/2026 11:23 | 02/23/2026 11:25 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 11:24 |  | N |  |  |  |  | 16W4 Circuit Breaker tripped and was slow to reclose at Maplewood Substation with no cause found. O&M to investigate reclosing timer. | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811755 | A
03/06/2026 15:45:36 | MECo | Bay State North | REVERE | SQUIRE RD | MAPLEWOOD 16 | 12-16W4 | 15 | OH | 19 | 0 | 28.69 | 544.98 | 02/23/2026 08:48 | 02/24/2026 13:29 | Unknown | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/24/2026 13:00 |  | N |  |  |  |  | Blown line fuses (2 of 3) P8 Squire Rd, no cause found. ABB Order Id: 871252 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810552 | A
03/06/2026 14:48:18 | MECo | Bay State North | SWAMPSCOTT | PURITAN RD | MEDFORD 9 | 12-9J2 | 5 | OH | 24 | 0 | 22.24 | 533.60 | 02/23/2026 04:04 | 02/24/2026 02:18 | Unknown | No failure or Unknown |  | SNOW | M | Y | Y | N | tc | 02/24/2026 01:00 |  | Y | Gino Cresta; | Email (gcresta@swampscottma.gov); |  |  | Blown B phase line fuse (1 of 3) P91 Puritan Rd due to unknown cause. ABB Order Id: 869963 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810392 | A
03/06/2026 14:43:31 | MECo | Bay State North | WINTHROP | SHIRLEY ST | METCALF SQUARE 96 | 12-96W1 | SY | OH | 2 | 0 | 41.60 | 83.20 | 02/23/2026 16:40 | 02/25/2026 10:17 | Tree Contact | Connector |  | WIND | M | N | Y | N | tc | 02/25/2026 09:30 |  | N |  |  |  |  | Tree limb took down service to house 916 Shirley Ave. ABB Order Id: 874123 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811744 | A
03/06/2026 14:28:27 | MECo | Bay State North | WINTHROP | PROSPECT AVE | METCALF SQUARE 96 | 12-96W1 | SY | OH | 2 | 0 | 9.95 | 19.90 | 02/24/2026 13:21 | 02/24/2026 23:19 | Failed Equipment | Conductors |  | SNOW | M | N | Y | N | tc | 02/24/2026 22:15 |  | N |  |  |  |  | Burnt up connectors and service to house 11 Prospect Ave, damaging neutral and hot leg and pole side connectors. ABB Order Id: 873667 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810866 | A
03/06/2026 14:16:36 | MECo | Bay State North | WINTHROP | PICO AVE | METCALF SQUARE 96 | 12-96W1 | 15 |  | 7 | 0 | 18.46 | 129.15 | 02/23/2026 11:05 | 02/24/2026 05:33 | Failed Equipment | Cutout - open |  | WIND | M | N | Y | N | tc | 02/24/2026 04:00 |  | N |  |  |  |  | Failed transformer cutout P1375 Pico Ave. ABB Order Id: 871992 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810432 | A
03/06/2026 14:13:10 | MECo | Bay State North | WINTHROP | VETERANS RD | METCALF SQUARE 96 | 12-96W1 | 15 | OH | 26 | 0 | 33.60 | 873.60 | 02/23/2026 06:54 | 02/24/2026 16:30 | Failed Equipment | Pole - wood |  | BLIZ | M | N | Y | N | tc | 02/24/2026 11:00 |  | N |  |  |  |  | Blown C phase line fuse (1 of 3) P1851 Veterans Rd caused by failed P1867 Veterans Rd during winter weather event. ABB Order Id: 870706, 873496 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810694 | A
03/06/2026 13:42:19 | MECo | Bay State North | WINTHROP | SHIRLEY ST | METCALF SQUARE 96 | 12-96W1 | 15 | OH | 464 | 0 | 20.77 | 9635.73 | 02/23/2026 07:44 | 02/24/2026 04:31 | Tree Contact | Insulator - pin or post |  | SNOW | M | Y | Y | N | tc | 02/23/2026 23:00 |  | Y | On Duty Officer;John Goodwin; | Email (fromeo@winthropma.gov);Email (jgoodwin@winthropma.gov); |  |  | Pole Top Recloser P412 Shirley St locked out caused by trees taking phase off pin P430 Shirley St and also past P1565 Tafts Ave multiple phases off pins. Customer count reduced by previously existing outage at P434 Shirley at Bayview. (Event 8811735) ABB Order Id: 870991 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810411 | A
03/06/2026 13:38:54 | MECo | Bay State North | WINTHROP | SHIRLEY ST | METCALF SQUARE 96 | 12-96W1 | 15 | OH | 95 | 0 | 22.46 | 2132.75 | 02/23/2026 06:03 | 02/24/2026 04:31 | Failed Equipment | Cutout - open |  | WIND | M | Y | Y | N | tc | 02/23/2026 21:00 |  | N |  |  |  |  | Pole Top Recloser P412 Shirley St tripped and reclosed caused by failed line fuse cutout P434 Shirley St at Bayview. Restoration delayed due to subsequent lockout same PTR during Winter Weather event with multiple trees taking down primary on circuit. Water main break towards the entrance to town also made access to Winthrop difficult and delayed restoration as well. Cutout was replaced de-energized then restored together once all damage was repaired. (Event 870991) | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811735 | A
03/06/2026 13:08:57 | MECo | Bay State North | WINTHROP | SHIRLEY ST | METCALF SQUARE 96 | 12-96W1 | 15 | OH | 51 | 0 | 2.37 | 120.70 | 02/23/2026 04:29 | 02/23/2026 06:51 | Unknown | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/23/2026 06:00 |  | N |  |  |  |  | Blown line fuse P441 Shirley St, cause unknown. ABB Order Id: 870020, 870031 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810258 | A
03/06/2026 12:25:03 | MECo | Bay State North | REVERE | BROADWAY ST | REVERE 7 | 12-7W2 | 15 | OH | 10 | 0 | 23.91 | 239.00 | 02/23/2026 08:31 | 02/24/2026 08:26 | Unknown | No failure or Unknown |  | SNOW | M | Y | Y | N | tc | 02/24/2026 08:00 |  | Y | Brendan O Regan;Scott Crabtree; | Email (boregan@saugus-ma.gov);Email (scrabtree@saugus-ma.gov); |  |  | Blown line fuses P3578 Salem Tpk. Patrol found no cause. ABB Order Id: 871196 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810440 | A
03/06/2026 12:00:11 | MECo | Bay State North | SALEM | COLUMBUS AVE | RAILYARD 49 | 12-49W6 | 5 | OH | 17 | 0 | 34.32 | 583.38 | 02/23/2026 07:33 | 02/24/2026 17:52 | Physical Interference / Company | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/24/2026 17:15 |  | N |  |  |  |  | Blown B phase line fuse (1 of 3) P4216 Columbus Ave caused by phase slap P1877 Winter Island Rd. ABB Order Id: 870894 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810732 | A
03/06/2026 11:53:27 | MECo | Bay State North | SALEM | WEBB ST | RAILYARD 49 | 12-49W6 | 15 | OH | 117 | 0 | 9.91 | 1158.30 | 02/23/2026 09:03 | 02/23/2026 18:58 | Unknown | No failure or Unknown |  | OTHR | M | Y | Y | N | tc | 02/23/2026 18:15 |  | N |  |  |  |  | Blown high side step down transformer fuse P3592 Webb St. Cause unknown. ABB Order Id: 871357 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810296 | A
03/06/2026 11:44:56 | MECo | Bay State North | SALEM | WEBB ST | RAILYARD 49 | 12-49W6 | 15 | OH | 110 | 0 | 19.96 | 2194.50 | 02/23/2026 07:37 | 02/24/2026 03:35 | Tree Contact | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/24/2026 03:00 |  | N |  |  |  |  | Blown B phase line fuse (1 of 3) P3601 Webb St caused by tree limb P1486 Washington N Sq. ABB Order Id: 870983 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810402 | A
03/06/2026 11:24:50 | MECo | Bay State North | SALEM | NORTHEY ST | RAILYARD 49 | 12-49W6 | 15 |  | 76 | 0 | 11.39 | 865.13 | 02/23/2026 07:35 | 02/23/2026 18:58 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 17:45 |  | N |  |  |  |  | Blown transformer fuse P1237 Northey St caused by tree limb during winter weather event. ABB Order Id: 870927, 872847, 872979 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810287 | A
03/06/2026 09:59:47 | MECo | Bay State North | SALEM | UNKNOWN71 ST | RAILYARD 49 | 12-49W4 | SY | OH | 321 | 0 | 0.35 | 112.35 | 02/24/2026 21:11 | 02/24/2026 21:33 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/24/2026 21:11 |  | N |  |  |  |  | While patrolling the 49W4 Circuit Breaker trip and reclose at Railyard Substation during a winter weather event the day prior, crews found tree limbs on primary P2717 Canal St and requested area de-energized to remove branch and pull slack from primary. Back fed most customers from P135 Essex St up to P1266 Canal St then opened 49W4 CB to make repairs. ABB Order Id: 874011 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810852 | A
03/06/2026 09:52:06 | MECo | Bay State North | SALEM | LORING AVE | RAILYARD 49 | 12-49W4 | 5 |  | 17 | 0 | 7.48 | 126.93 | 02/24/2026 16:30 | 02/24/2026 23:58 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/24/2026 18:00 |  | N |  |  |  |  | Crews manually disconnected transformer P2597 Loring Ave to repair secondary neutral that was damaged by tree. ABB Order Id: 872715 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810863 | A
03/05/2026 16:11:05 | MECo | Bay State North | ROCKPORT | POOLE'S LN | ROCKPORT 40 | 12-40J1 | 5 | OH | 1002 | 0 | 3.10 | 3106.20 | 02/24/2026 14:09 | 02/24/2026 17:15 | Animal | Switch - Solid Blades |  | NORM | M | Y | Y | N | tc | 02/24/2026 14:45 |  | N |  |  |  |  | 40J1 circuit breaker at Rockport sub locked out. Cause: Animal contact broke porcelain enclosed disconnect P2089-1 Pooles Ln. ABB Order Id: 873713 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810828 | A
03/04/2026 13:31:32 | MECo | Bay State North | LYNN | IRVING RD | REVERE 7 | 12-7J903 | SY |  | 426 | 0 | 0.27 | 113.60 | 02/25/2026 17:00 | 02/25/2026 17:16 | Failed Equipment | Substation device other |  | NORM | M | Y | Y | N | tc | 02/25/2026 17:00 |  | Y | Brendan O Regan;Scott Crabtree; | Email (boregan@saugus-ma.gov);Email (scrabtree@saugus-ma.gov); |  |  | De-energized 7J903 Circuit Breaker at Hudson 7 Substation to drop and pick 7J3 customers onto feeder tie. Offload was needed to establish clearance and repair failed 240 CB trip coil at Hudson. ABB Order Id: 874418 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811136 | A
03/04/2026 13:03:32 | MECo | Bay State North | LYNN | HUDSON TER | REVERE 7, REVERE 7, REVERE 7 | 12-1387, 12-7J901, 12-7J902, 12-7J903 | 15 | OH | 1513 | 0 | 17.44 | 10915.40 | 02/23/2026 06:36 | 02/24/2026 00:02 | Failed Equipment | Conductors |  | WIND | M | Y | Y | N | tc | 02/23/2026 07:00 |  | Y | Brendan O Regan;Scott Crabtree; | Email (boregan@saugus-ma.gov);Email (scrabtree@saugus-ma.gov); |  |  | 1387 Circuit Breaker locked out at Lynn Substation caused by Aerial cable fault P107 Boston St. Hudson 7 Sub dead bus transfer operated but 240 CB never opened due to a burned up trip coil. When the 1240 tie CB closed, the 140 CB locked out from energizing the 1387 Aerial cable issue. This resulting in an outage to all Hudson 7 customers. Patrolled each feeder prior to re-energizing. 1387 customers restored on alternate SWGR supply. ABB Order Id: 870744, 870800, 870801, 872334, 871818 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810275 | A
03/04/2026 10:39:59 | MECo | Bay State North | NAHANT | WILSON RD |  | 12-1391 | 5 |  | 10 | 0 | 10.49 | 104.83 | 02/23/2026 06:24 | 02/23/2026 16:53 | Failed Equipment | Cutout - open |  | SNOW | M | N | Y | N | tc | 02/23/2026 16:00 |  | N |  |  |  |  | Burnt up transformer cutout P38 Wilson Rd. ABB Order Id: 870439, 871236, 872196, 872496 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810238 | A
03/04/2026 10:28:57 | MECo | Bay State North | LYNN | LYNN GAS ST | BEVERLY 12, BEVERLY 12 | 12-12J904, 12-1392, 12-12J903 | 15 | OH | 2217 | 0 | 3.81 | 2325.07 | 02/23/2026 09:45 | 02/23/2026 13:33 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 11:00 |  | N |  |  |  |  | 1392 Circuit Breaker locked out at Lynn Substation during winter weather event. This caused a loss of supply to Granite 12 substation whose transfer did not operate right away due to a slow to close 1240 tie CB, resulting in an outage to 12J903 and 12J904 customers. Bridge St 6 Substation transferred properly to the 1386 supply. With no cause found on overhead patrol, restored 1392 customers at 175 Lynnway SWGR and 164 Commercial St SWGR on their alternate supply. Underground supervisor requested we close CB due to absence of ground targets on lockout, which held. No cause found. ABB Order Id: 871541 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810330 | A
03/04/2026 09:30:59 | MECo | Bay State North | SWAMPSCOTT | STETSON AVE | WINTHROP 22 | 12-22W2 | 5 | OH | 1 | 0 | 33.25 | 33.23 | 02/23/2026 11:00 | 02/24/2026 20:15 | Failed Equipment | Conductors |  | NORM | M | N | Y | N | tc | 02/24/2026 18:30 |  | N |  |  |  |  | Failed service to house 147 Stetson Ave. ABB Order Id: 871979 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810853 | A
03/04/2026 09:11:25 | MECo | Bay State North | SALEM | 2370 HI-LINE RWAY RWAY | WINTHROP 22, WINTHROP 22 | 12-2370, 12-22W1, 12-22W3 | SY |  | 3265 | 0 | 35.04 | 6013.58 | 02/23/2026 06:23 | 02/24/2026 17:26 | Tree Contact | Switch - Solid Blades |  | WIND | M | Y | Y | N | tc | 02/23/2026 07:30 |  | Y | Gino Cresta;, Gino Cresta; | Email (gcresta@swampscottma.gov);, Email (gcresta@swampscottma.gov); |  |  | 2370 Circuit Breaker locked out at Railyard Substation caused by tree on primary 2370 ROW at Load Break 70-18 Salem State University Atlantic Hall. This caused a loss of supply to 22W1 and 22W3 customers at Swampscott substation. High side line transfer did not operate properly at Swampscott due issue with 11T CB undervoltage contact. Crews manually restored all Swampscott customers via BT CB. Removed tree from primary on the 2370 but immediately de-energized when crew at Railyard saw 70-3 disconnect arcing. Took clearance to make repairs then closed 2370 CB for final restore. ABB Order Id: 870488, 870470 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810323 | A
03/04/2026 08:01:28 | MECo | Bay State North | WINTHROP | PAULINE ST | WINTHROP 22 | 12-22J2 | 25 | OH | 11 | 0 | 11.82 | 129.98 | 02/24/2026 08:45 | 02/24/2026 20:34 | Unknown | No failure or Unknown |  | SNOW | M | Y | Y | N | tc | 02/24/2026 15:00 |  | Y | On Duty Officer;John Goodwin; | Email (fromeo@winthropma.gov);Email (jgoodwin@winthropma.gov); |  |  | Blown line fuse (1 of 3) P1654 Pauline St with no cause found on overhead primary. Isolated underground section of cable opening center phase riser P3 Woodside Ave and restored the part power to customers on OH section. Cable tested good, no cause found. ABB Order Id: 873411 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810826 | A
03/04/2026 07:54:55 | MECo | Bay State North | WINTHROP | ARGYLE ST | WINTHROP 22 | 12-22J7 | 5 | OH | 506 | 0 | 22.33 | 6498.63 | 02/23/2026 07:23 | 02/24/2026 05:42 | Physical Interference / Company | No failure or Unknown |  | NORM | M | Y | Y | N | tc | 02/23/2026 17:00 |  | Y | On Duty Officer;John Goodwin; | Email (fromeo@winthropma.gov);Email (jgoodwin@winthropma.gov); |  |  | 22J7 Circuit Breaker locked out at Winthrop substation caused by phases slapping together on Argyle St during winter weather event. Customer past fuse P819 Main St restored after tree was cleared from primary P979 Marshall St. ABB Order Id: 870845, 872782 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810420 | A
03/04/2026 07:40:28 | MECo | Bay State North | WINTHROP | CREST AVE | WINTHROP 22 | 12-22J6 | 5 | OH | 23 | 0 | 19.83 | 455.78 | 02/23/2026 10:38 | 02/24/2026 06:28 | Physical Interference / Company | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/24/2026 06:00 |  | N |  |  |  |  | Blown B and C line fuses (2 of 3) P130 Crest Ave caused by phase slap during winter weather event. ABB Order Id: 873141 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810427 | A
03/04/2026 07:34:44 | MECo | Bay State North | WINTHROP | ARGYLE ST | WINTHROP 22 | 12-22J5 | 5 | OH | 926 | 0 | 20.36 | 6794.10 | 02/23/2026 04:31 | 02/24/2026 00:53 | Failed Equipment | Tap |  | WIND | M | Y | Y | N | tc | 02/23/2026 23:00 |  | Y | On Duty Officer;John Goodwin; | Email (fromeo@winthropma.gov);Email (jgoodwin@winthropma.gov); |  |  | 22J5 Circuit Breaker tripped and reclosed at Winthrop substaion caused by failed C phase tap P103 Wintrhop Parkway during winter weather event. Opened CB to repair tap de-energized. Restoration delayed due to town water main break restricting access to Winthrop. ABB Order Id: 870595 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810373 | A
03/03/2026 16:40:04 | MECo | Bay State North | WINTHROP | REVERE ST | WINTHROP 22 | 12-22J1 | 5 | OH | 696 | 0 | 10.57 | 7354.40 | 02/23/2026 06:36 | 02/23/2026 17:10 | Physical Interference / Company | Conductors |  | SNOW | M | Y | Y | N | tc | 02/23/2026 07:00 |  | Y | On Duty Officer;John Goodwin; | Email (fromeo@winthropma.gov);Email (jgoodwin@winthropma.gov); |  |  | 22J1 Circuit Breaker locked out at Winthrop substation caused by phase slap during high wind winter weather event with primary parting P82 Quincy Ave. Restoration delayed due to town water main break that flooded streets and limited access into town. ABB Order Id: 870568 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811509 | A
03/03/2026 16:29:38 | MECo | Bay State North | WINTHROP | ARGYLE ST | WINTHROP 22 | 12-22J3 | 5 | OH | 1033 | 0 | 12.72 | 963.60 | 02/23/2026 06:33 | 02/23/2026 19:16 | Physical Interference / Company | Tap |  | SNOW | M | Y | Y | N | tc | 02/23/2026 18:00 |  | Y | On Duty Officer;John Goodwin; | Email (fromeo@winthropma.gov);Email (jgoodwin@winthropma.gov); |  |  | Failed C phase tap load side of Load Break P185 Shirley St caused by phase slap during winter weather event at P1035 Cross St at Franklin. Opened 22J3 Circuit Breaker at Winthrop Substation to make repairs. Restoration was delayed due to town water main break that flooded entrance to the town of Winthrop. ABB Order Id: 872867, 870536 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811510 | A
03/03/2026 15:51:38 | MECo | Bay State North | LYNN | HOBSON ST | LYNN 21 | 12-21J37 | SY | OH | 1 | 0 | 17.91 | 17.90 | 02/23/2026 10:14 | 02/24/2026 04:09 | Failed Equipment | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 02:00 |  | N |  |  |  |  | Failed service to house 17 Hobson St during winter storm event. ABB Order Id: 871790 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810407 | A
03/03/2026 15:46:36 | MECo | Bay State North | LYNN | LYNN GAS ST | LYNN 21 | 12-21J33 | 5 | OH | 378 | 0 | 16.39 | 4302.13 | 02/23/2026 06:17 | 02/23/2026 22:40 | Failed Equipment | Insulator - pin or post |  | WIND | M | N | Y | N | tc | 02/23/2026 07:00 |  | N |  |  |  |  | 21J33 Circuit Breaker locked out at Lynn Substation due to failed pin and primary down P23 Alley St. Opened P27-1 Alley and closed CB. Crews tied primary back up and closed 27-1 Alley restoring all customers. ABB Order Id: 870417 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810355 | A
03/03/2026 12:49:47 | NanECo | Bay State South | NANTUCKET | OLD SOUTH RD | CANDLE STREET 101 | 04-101L7 | 5 |  | 12 | 0 | 91.54 | 449.50 | 02/23/2026 17:57 | 02/27/2026 13:30 | Failed Equipment | Overhead Device Other |  | WIND | M | N | Y | N | tc | 02/26/2026 15:00 |  | N |  |  |  |  | Blown transformer fuse P35 Old South Rd. Downed secondaries due to broken bracket. Made temporary repairs 2/26/26, some customers still had part power. Manually opened transformer fuse again next morning to make permanent repairs. ABB Order Id: 873274, 874683 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811226 | A
03/03/2026 11:46:36 | MECo | Bay State North | HAVERHILL | RAILROAD ST | EAST BRADFORD 65 | 14-65L3 | SY | OH | 52 | 0 | 1.31 | 67.60 | 02/23/2026 17:26 | 02/23/2026 18:45 | Physical Interference / Other | Pole - wood |  | WIND | M | N | Y | N | tc | 02/23/2026 17:26 |  | N |  |  |  |  | Crew opened high side step down transformer fuses P6 Railroad St to lash broken P6 Railroad to a new pole set at that location. Cause was an MVA. ABB Order Id: 872754, 872808 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811488 | A
03/03/2026 11:38:49 | MECo | Bay State North | HAVERHILL | WEBSTER ST | WATER STREET 31 | 14-31L2 | 5 | OH | 5 | 0 | 5.61 | 28.00 | 02/23/2026 20:04 | 02/24/2026 01:40 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/23/2026 22:45 |  | N |  |  |  |  | Tree took down service to house 15 Webster St and also damaged meter. ABB Order Id: 873025, 872936 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810385 | A
03/03/2026 11:19:22 | MECo | Bay State North | WESTFORD | DUNSTABLE RD | WESTFORD 57 | 14-57L3 | 15 | OH | 11 | 0 | 2.64 | 28.97 | 02/23/2026 13:43 | 02/23/2026 16:21 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/23/2026 14:45 |  | N |  |  |  |  | Blown line fuse P28 Dunstable Rd caused by tree limb breaking primary P4 Long Rd. ABB Order Id: 872424 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810224 | A
03/03/2026 10:39:33 | MECo | Bay State North | LAWRENCE | WEST ST | NORTH CHELMSFORD 2, BILLERICA 6 | 14-2J2, 14-6J5 | 5 | OH | 932 | 0 | 27.12 | 2775.67 | 02/23/2026 12:04 | 02/24/2026 15:12 | Failed Equipment | Tap |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 13:00 |  | Y | Lawrence Police Department; | Email (disorder@lawpd.com); |  |  | 6J5 Circuit Breaker locked out at N Lawrence substation on a suspected cable fault during Winter Storm. Overhead initially patrolled clear. Opened cable riser disconnects P1225 Methuen St and restored customers up to P1012 Bennett St via P1227 Methuen St. Customers past P1012 Bennett restored via P1633 Winter St. Opened 2J2 CB at Lawrence 2 to close OFCs de-energized and restored MH291 and MH292 Broadway customers via 2J2. Cable tested good, patrolled again and found failed B phase tap and primary burnt up on telephone line P1459 Essex St. All commercial 3 phase customers past this location were part powered. Opened P1633 Winter, de-energizing customers back to P1012 Bennett to make repairs. ABB Order Id: 872824, 872144 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811484 | A
03/03/2026 08:23:08 | MECo | Bay State North | ANDOVER | WILDWOOD RD | BURTT ROAD 54 | 14-54L3 | 15 | OH | 43 | 0 | 6.25 | 181.97 | 02/23/2026 11:51 | 02/23/2026 18:06 | Tree Contact | Transformer Other |  | WIND | M | N | Y | N | tc | 02/23/2026 14:00 |  | N |  |  |  |  | Blown fuse P6504 Wildwood Rd caused by tree taking down primary and damaging transformer P6964 Sequoia Ln which remained out until replaced. ABB Order Id: 872098 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810261 | A
03/03/2026 07:13:55 | MECo | Bay State North | SALISBURY | TRUE RD | BEACH ROAD 7 | 14-7L4 | 15 | OH | 2 | 0 | 7.94 | 15.87 | 02/23/2026 11:34 | 02/23/2026 19:30 | Tree Contact | Conductors |  | BLIZ | M | N | Y | N | tc | 02/23/2026 15:00 |  | N |  |  |  |  | Blown line fuse P17 True Rd caused by tree taking down primary and secondary P17-3. ABB Order Id: 872068 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810306 | A
03/03/2026 07:04:09 | MECo | Bay State North | HAVERHILL | LAFAYETTE ST | NORTH HAVERHILL 48 | 14-48L2 | 15 | OH | 36 | 0 | 4.79 | 172.20 | 02/23/2026 11:31 | 02/23/2026 16:19 | Failed Equipment | Tap |  | WIND | M | N | Y | N | tc | 02/23/2026 13:30 |  | N |  |  |  |  | Failed tap to transformer cutout P5 Lafayette St. ABB Order Id: 872064 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810241 | A
03/03/2026 06:54:45 | MECo | Bay State North | METHUEN | PELHAM ST | EAST DRACUT 75 | 14-75L3 | 15 | OH | 87 | 0 | 1.56 | 117.28 | 02/23/2026 11:25 | 02/23/2026 12:59 | Tree Contact | Conductors |  | WIND | M | Y | Y | N | tc | 02/23/2026 11:45 |  | N |  |  |  |  | Tree fell and broke primary P1324 Pelham St at Salem St. Opened A phase line fuse (1 of 3) P1315 Pelham St to remove tree and make repairs. ABB Order Id: 872061,872120 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810193 | A
03/03/2026 06:28:46 | MECo | Bay State North | BILLERICA | TERCENTENNIAL DR | BILLERICA 70 | 14-70L6 | 15 | OH | 51 | 0 | 32.90 | 1663.40 | 02/23/2026 11:05 | 02/24/2026 20:00 | Tree Contact | Pole - wood |  | WIND | M | N | Y | N | tc | 02/23/2026 13:00 |  | N |  |  |  |  | Blown line fuse P24 Tercentennial Dr caused by tree that fell and broke P3 Ichabod Ln and also damaged service to house 3 Ichabod which remained out for duration. Crews replaced pole and closed fuse. ABB Order Id: 871994 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810425 | A
03/03/2026 06:04:50 | MECo | Bay State North | BILLERICA | TREBLE COVE RD | BILLERICA 70 | 14-70L5 | 5 | OH | 15 | 0 | 1.54 | 23.00 | 02/23/2026 10:49 | 02/23/2026 12:22 | Tree Contact | No failure or Unknown |  | BLIZ | M | N | Y | N | tc | 02/23/2026 12:00 |  | N |  |  |  |  | Blown line fuse P79 Treble Cove Rd caused by tree branch P1 Shedd Rd. ABB Order Id: 871942 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810154 | A
03/01/2026 15:54:52 | MECo | Bay State North | NORTH ANDOVER | SALEM ST | WOODCHUCK HILL | 14-56L2 | 15 | OH | 211 | 0 | 4.50 | 823.37 | 02/23/2026 10:36 | 02/23/2026 15:06 | Tree Contact | Insulator - pin or post |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 12:00 |  | N |  |  |  |  | Blown line fuse P3238 Salem caused by tree falling P4 Ingalls St breaking insulator at that location. Opened P48 Forest St to isolate broken crossarm P33 Lacey St prior to energizing Ingalls. ABB Order Id: 871910, 872535 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810250 | A
03/01/2026 15:30:54 | MECo | Bay State North | ANDOVER | LOWELL ST | BALLARDVALE 50 | 14-50L1 | 15 | OH | 9 | 0 | 25.82 | 232.35 | 02/23/2026 10:00 | 02/24/2026 11:50 | Tree Contact | Conductors |  | NORM | M | N | Y | N | tc | 02/23/2026 12:00 |  | N |  |  |  |  | Blown line fuse P506 Lowell St caused tree breaking primary P6498 Kirkland Dr. ABB Order Id: 871697 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810509 | A
03/01/2026 15:24:51 | MECo | Bay State North | LOWELL | LAKEVIEW AVE | HOOVER STREET 21 | 14-21L2 | SY | OH | 260 | 0 | 0.19 | 47.67 | 02/23/2026 10:00 | 02/23/2026 10:12 | Physical Interference / Other | Pole - wood |  | WIND | M | Y | Y | N | tc | 02/23/2026 10:00 |  | Y | Greg Hudon; | Email (ghudon@lowellma.gov); |  |  | Manually opened line fuses P31 Lakeview Ave to repair broken P21 West Sixth St. Cause: MVA. ABB Order Id: 871695 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810126 | A
03/01/2026 14:22:47 | MECo | Bay State North | HAVERHILL | SOUTH MAIN ST | WARD HILL 43 | 14-43L3 | 15 |  | 15 | 0 | 11.15 | 167.25 | 02/23/2026 07:51 | 02/23/2026 19:00 | Failed Equipment | Cutout - open |  | WIND | M | Y | Y | N | tc | 02/23/2026 11:30 |  | N |  |  |  |  | Failed Transformer cutout P33 S Main St ABB Order Id: 871010, 871844, 872386 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810144 | A
03/01/2026 14:06:07 | MECo | Bay State North | NEWBURY | PLUM ISLAND TPKE | NEWBURY 60 | 14-60L1 | SY | OH | 1286 | 0 | 8.82 | 11338.23 | 02/24/2026 00:24 | 02/24/2026 09:13 | Tree Contact | Pole - wood |  | NORM | M | Y | Y | N | tc | 02/24/2026 00:24 |  | N |  |  |  |  | Pole Top Recloser P77 Plum Island Tpk tripped and reclosed caused by a tree falling and breaking P55 Plum Island Tpk. Manually opened P31 Plumb Island Tpk to make repairs. ABB Order Id: 873124 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810459 | A
03/01/2026 13:53:33 | MECo | Bay State North | NEWBURY | HIGH RD | NEWBURY 60 | 14-60L1 | 5 | OH | 1 | 0 | 10.36 | 10.35 | 02/23/2026 08:36 | 02/23/2026 18:58 | Failed Equipment | Cutout - enclosed |  | BLIZ | M | N | Y | N | tc | 02/23/2026 16:00 |  | N |  |  |  |  | Failed enclosed line fuse cutout box P99 High Rd. ABB Order Id: 871220 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810292 | A
03/01/2026 13:48:46 | MECo | Bay State North | NEWBURY | SUNSET DR | NEWBURY 60 | 14-60L1 | 15 | OH | 17 | 0 | 4.95 | 83.87 | 02/23/2026 07:27 | 02/23/2026 12:24 | Tree Contact | Overhead Device Other |  | WIND | M | N | Y | N | tc | 02/23/2026 09:00 |  | N |  |  |  |  | Blown line fuse P13 Sunset Dr caused by tree limb taking phase off pin P4 Harvard Way. ABB Order Id: 870869 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810161 | A
03/01/2026 13:39:19 | MECo | Bay State North | LOWELL | SHIRLEY AVE | BOULEVARD 77 | 14-77L2 | 15 | OH | 28 | 0 | 3.02 | 84.47 | 02/23/2026 05:58 | 02/23/2026 09:00 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 08:30 |  | N |  |  |  |  | Blown riser fuse (1 of 3) P2 Shirley Ave during winter weather event with no cause reported. Overrode customer count to more accurately reflect 3 phase residential customers affected. ABB Order Id: 870333 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810120 | A
03/01/2026 13:15:42 | MECo | Bay State North | ROCKPORT | GOTT AVE | RIVERDALE 52 | 12-52L1 | 5 |  | 11 | 0 | 21.18 | 233.02 | 02/24/2026 19:04 | 02/25/2026 16:15 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/25/2026 10:40 |  | N |  |  |  |  | Blown line fuse P937 Gott Ave caused by tree taking down several spans on primary P944 Gott. ABB Order Id: 874113, 847336, 873971 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811025 | A
03/01/2026 13:12:23 | MECo | Bay State North | NEWBURY | NORTH MAIN ST | BYFIELD 34 | 14-34M1 | 5 | OH | 70 | 0 | 3.91 | 262.50 | 02/23/2026 05:07 | 02/23/2026 09:01 | Tree Contact | Conductors |  | WIND | M | Y | Y | N | tc | 02/23/2026 05:45 |  | Y | Mike Dwyer; | Email (dwyer@westnewburysafety.org); |  |  | Tree fell and broke primary P11 Moulton St. Manually opening fuse P44 N Main St to repair. ABB Order Id: 870154 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810118 | A
03/01/2026 12:02:21 | MECo | Bay State North | TEWKSBURY | BROWN ST | EAST TEWKSBURY 59 | 14-59L3 | 5 | OH | 57 | 0 | 26.82 | 162.30 | 02/23/2026 05:07 | 02/24/2026 07:56 | Tree Contact | Pole - wood |  | WIND | M | N | Y | N | tc | 02/23/2026 06:00 |  | N |  |  |  |  | Blown line fuse P32 Brown St caused by tree falling and breaking pole and transformer P19 Nevada Rd. Isolated damage and closed P32 Brown. Customers off P19 Nevada out for duration of repairs. ABB Order Id: 870163, 871057 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810825 | A
03/01/2026 11:52:17 | MECo | Bay State North | TEWKSBURY | MAIN ST | EAST TEWKSBURY 59 | 14-59L3 | 5 | OH | 106 | 0 | 31.49 | 1916.55 | 02/23/2026 05:11 | 02/24/2026 12:40 | Tree Contact | Pole - wood |  | WIND | M | Y | Y | N | tc | 02/23/2026 06:40 |  | Y | Ryan Columbus; | Email (rcolumbus@tewksbury-ma.gov); |  |  | Blown high side stepdown transformer fuses P285 Main St caused by tree taking down poles P10 - P13 Vernon St. Customers from P10 Vernon down St Mary's remained out for duration of repair. ABB Order Id: 870167, 872966 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810331 | A
03/01/2026 11:27:28 | MECo | Bay State North | LOWELL | FUTURE RD | POWER COMPANY RD | 14-20L2 | 15 | OH | 67 | 0 | 2.58 | 171.97 | 02/23/2026 04:20 | 02/23/2026 06:55 | Unknown | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/23/2026 05:30 |  | N |  |  |  |  | Blown line fuse P64 Lawrence St during winter weather event, cause not given. ABB Order Id: 870246 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811383 | A
03/01/2026 11:22:53 | MECo | Bay State North | SALISBURY | NORTH END BLVD | BEACH ROAD 7 | 14-7L1 | 15 | OH | 11 | 0 | 9.71 | 106.70 | 02/23/2026 07:17 | 02/23/2026 17:00 | Unknown | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 15:00 |  | N |  |  |  |  | Blown line fuse P57 North End Blvd during weather event with no cause given. ABB Order Id: 870812 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810278 | A
03/01/2026 11:19:29 | MECo | Bay State North | SALISBURY | NORTH END BLVD | BEACH ROAD 7 | 14-7L1 | 15 | OH | 81 | 0 | 11.69 | 946.35 | 02/23/2026 05:05 | 02/23/2026 16:47 | Unknown | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 16:00 |  | N |  |  |  |  | Blown line fuse P6 North End Blvd during weather event with no cause given. ABB Order Id: 870200, 872481 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810168 | A
03/01/2026 11:13:09 | MECo | Bay State North | SALISBURY | BROADWAY ST | BEACH ROAD 7 | 14-7L1 | 15 | OH | 638 | 0 | 8.29 | 4561.77 | 02/23/2026 04:47 | 02/23/2026 13:05 | Tree Contact | Conductors |  | SNOW | M | Y | Y | N | tc | 02/23/2026 05:45 |  | N |  |  |  |  | Blown B phase line fuse (1 of 3) caused by tree taking down primary P23 Railroad Ave. Manually opened remaining fuses to de-energize until crews were available to repair. ABB Order Id: 870067 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810184 | A
02/28/2026 16:15:22 | MECo | Bay State South | WESTPORT | NARROW AVE | BATES 115 | 05-115W45 | 15 | OH | 6 | 0 | 30.98 | 185.80 | 02/23/2026 06:48 | 02/24/2026 13:47 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/24/2026 12:00 |  | N |  |  |  |  | Blown 25K line fuse P8 Narrow Rd aka Armory Pettey Rd. Tree limb took phase off pin at P8-1. Blizzard 2026. ABB Order Id: 872942 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810575 | A
02/28/2026 16:10:12 | MECo | Bay State South | WESTPORT | EAST BRIGGS RD | BATES 115 | 05-115W45 | 5 |  | 8 | 0 | 34.88 | 278.93 | 02/23/2026 05:32 | 02/24/2026 16:25 | Tree Contact | Pole - wood |  | WIND | M | N | Y | N | tc | 02/24/2026 13:53 |  | N |  |  |  |  | Blown transformer fuse P3 Briggs Rd. Tree limb took down secondary and pole at 332 Briggs Rd. Blizzard 2026. Also needs electrician. ABB Order Id: 870236 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810684 | A
02/28/2026 13:07:51 | MECo | Bay State South | FALL RIVER | COUNTY ST | HATHAWAY | 05-106W44 | 15 | OH | 42 | 0 | 27.82 | 1168.30 | 02/23/2026 08:26 | 02/24/2026 12:15 | Failed Equipment | Tap |  | WIND | M | N | Y | N | tc | 02/24/2026 11:45 |  | N |  |  |  |  | Blown 15K line fuse at P56 County St .Broken primary tap P1 Keeley St. Roads not plowed, waiting on the town of Fall River to plow road. Blizzard 2026. ABB Order Id: 871178 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810517 | A
02/28/2026 11:15:17 | MECo | Bay State South | NORWELL | SOUTH ST | NORWELL SUB | 07-96W44 | SY | OH | 1 | 0 | 20.73 | 20.72 | 02/23/2026 19:55 | 02/24/2026 16:39 | Tree Contact | Connector |  | WIND | M | N | Y | N | tc | 02/24/2026 15:30 |  | N |  |  |  |  | Tree fell and took down service drop to 125 South St. ABB Order Id: 872917 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810686 | A
02/27/2026 16:06:13 | MECo | Bay State North | BEVERLY | RIVER ST | BEVERLY 12 | 12-12L4 | 15 | UG | 0 | 0 | 1.00 | 0.00 | 02/25/2026 22:03 | 02/25/2026 23:03 | Failed Equipment | Splice |  | NORM | M | Y | Y | N | tc | 02/25/2026 22:35 |  | N |  |  |  |  | 12L4 Circuit Breaker locked out at Beverly substation caused by failed H-Bodys MH2 River St. Opened P2402 Park St and closed P318 Elliott St to restore all customers. ABB Order Id: 874482 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811151 | A
02/27/2026 15:57:15 | MECo | Bay State West | SUTTON | ROUTE 146 ST | MILLBURY 4 | 01-304W6 | 15 | OH | 3 | 0 | 4.29 | 12.85 | 02/23/2026 15:48 | 02/23/2026 20:06 | Tree Contact | Overhead Device Other |  | WIND | M | N | Y | N | tc | 02/23/2026 19:00 |  | N |  |  |  |  | Blown line fuses (2 of 3) P3 Route 146 ROW off P81 due to tree knocking phase off pin in ROW P4. ABB Order Id: 872620 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811298 | A
02/27/2026 14:21:15 | MECo | Bay State West | DUDLEY | DUDLEY RD W ST | SNOW STREET 413 | 01-413L3 | 15 | OH | 7 | 0 | 5.58 | 28.08 | 02/23/2026 11:29 | 02/23/2026 17:04 | Tree Contact | Pole - wood |  | SNOW | M | N | Y | N | tc | 02/23/2026 12:48 |  | N |  |  |  |  | Tree fell and broke P7 Fish Rd and damaged service to house 34 Fish Rd. Crew opened line fuse P11 Dudley Rd W to make repairs. ABB Order Id: 872058, 872336 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810242 | A
02/27/2026 14:12:17 | MECo | Bay State West | DUDLEY | BRANDON RD | EAST WEBSTER 412 | 01-412L5 | 15 |  | 11 | 0 | 1.82 | 19.98 | 02/23/2026 10:57 | 02/23/2026 12:47 | Failed Equipment | Tap |  | SNOW | M | N | Y | N | tc | 02/23/2026 12:15 |  | N |  |  |  |  | Blown transformer fuse P23 Brandon Rd caused by failed high side tap to cutout. ABB Order Id: 871974, 872077 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810180 | A
02/27/2026 13:37:32 | MECo | Bay State West | PEPPERELL | WEST ST | GROTON STREET 226 | 01-226L2 | 5 | OH | 100 | 0 | 3.00 | 217.70 | 02/23/2026 12:01 | 02/23/2026 15:01 | Tree Contact | Crossarm |  | WIND | M | N | Y | N | tc | 02/23/2026 13:45 |  | N |  |  |  |  | Tree fell and broke primary and crossarm P36 West St. Crew manually opened step down fuse P55 West St to make repairs. ABB Order Id: 872148 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810213 | A
02/27/2026 13:06:21 | MECo | Bay State West | CHARLTON | SAUNDERSDALE RD | SNOW STREET 413 | 01-413L3 | 15 | OH | 144 | 0 | 1.63 | 235.20 | 02/23/2026 09:54 | 02/23/2026 11:32 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/23/2026 11:00 |  | N |  |  |  |  | Blown line fuse P24 Saundersdale Rd caused by tree damaging primary P6 Saunderdale Rd. ABB Order Id: 871676 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810147 | A
02/27/2026 12:24:34 | MECo | Bay State West | WEST BROOKFIELD | WARE RD | LASHAWAY 525 | 01-525L2 | 15 | OH | 524 | 0 | 2.30 | 1205.20 | 02/23/2026 08:50 | 02/23/2026 11:09 | Tree Contact | No failure or Unknown |  | BLIZ | M | Y | Y | N | tc | 02/23/2026 10:00 |  | N |  |  |  |  | Blown line fuses (3 of 3) P4 Ware Rd caused by tree on primary P17 Ware Rd. ABB Order Id: 871293 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810135 | A
02/27/2026 10:12:12 | MECo | Bay State West | LEICESTER | MOOSE HILL RD | LEICESTER 21 | 01-21W1 | 15 | OH | 10 | 0 | 8.38 | 43.47 | 02/23/2026 06:16 | 02/23/2026 14:40 | Tree Contact | Pole - wood |  | WIND | M | N | Y | N | tc | 02/23/2026 09:30 |  | N |  |  |  |  | Blown transformer fuse P7 Pryor Rd caused by tree that fell and damaged top of P7 Pryor. Opened line fuse P38 Moose Hill Rd to make temp repairs. ABB Order Id: 870407, 871443, 872124 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810201 | A
02/27/2026 09:20:19 | MECo | Bay State West | SUTTON | MANCHAUG RD | MILLBURY 4 | 01-304W6 | 15 | OH | 10 | 0 | 2.37 | 23.67 | 02/23/2026 07:18 | 02/23/2026 09:41 | Tree Contact | Overhead Device Other |  | WIND | M | N | Y | N | tc | 02/23/2026 08:00 |  | N |  |  |  |  | Blown line fuse P90 Manchuag Rd. Cause was tree limb took phase off pin at P96 Manchaug Rd. ABB Order Id: 870823 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810123 | A
02/27/2026 09:03:30 | MECo | Bay State West | DUNSTABLE | HOLLIS ST | DUNSTABLE 210 | 01-210L1 | 15 | OH | 49 | 0 | 4.47 | 218.87 | 02/23/2026 09:41 | 02/23/2026 14:09 | Tree Contact | Conductors |  | WIND | M | Y | Y | N | tc | 02/23/2026 10:00 |  | Y | Paul Zbikowski;Groton Dispatch; | Email (pzbikowski@dunstable-ma.gov);Email (police@grotonma.gov); |  |  | Blown line fuse P26 Hollis St. Cause was tree took primary down at P42 Hollis St. ABB Order Id: 871537 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810189 | A
02/27/2026 08:57:56 | MECo | Bay State West | WORCESTER | RICHMOND AVE | CHANDLER STREET 2 | 01-2J335 | SY | OH | 6 | 0 | 5.68 | 34.00 | 02/23/2026 09:50 | 02/23/2026 15:31 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/23/2026 12:00 |  | N |  |  |  |  | Tree fell and ripped down service drops to houses 61 and 63 Richmond Ave. ABB Order Id: 871576 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810208 | A
02/27/2026 08:27:24 | MECo | Bay State West | ATHOL | SOUTH WEST ST | CHESTNUT HILL 702 | 09-702W2 | 15 | OH | 29 | 0 | 1.07 | 30.93 | 02/23/2026 13:57 | 02/23/2026 15:01 | Failed Equipment | Lightning arrester |  | SNOW | M | Y | Y | N | tc | 02/23/2026 14:40 |  | N |  |  |  |  | Blown A phase high side step down transformer fuse (1 of 3) P17 South West St caused by failed LA at Step down P17-2 South West. Overrode customer count to reflect 1 of 3 residential 3 phase customers affected. ABB Order Id: 872443 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810199 | A
02/27/2026 08:17:29 | MECo | Bay State West | SUTTON | BOSTON WEST RD | MILLBURY 4 | 01-304W6 | 15 | OH | 15 | 0 | 3.15 | 47.00 | 02/23/2026 15:55 | 02/23/2026 19:04 | Tree Contact | Conductors |  | WIND | M | N | Y | N | tc | 02/23/2026 16:30 |  | N |  |  |  |  | Blown line fuse P91 W Boston Rd. Cause was tree took primary and secondary down at P3 Rich Rd. ABB Order Id: 872643 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810290 | A
02/27/2026 07:52:52 | MECo | Bay State West | DUDLEY | WOODSTOCK ST RD | EAST WEBSTER 412 | 01-412L4 | 15 |  | 13 | 0 | 2.74 | 35.53 | 02/23/2026 19:43 | 02/23/2026 22:28 | Failed Equipment | Tap |  | WIND | M | N | Y | N | tc | 02/23/2026 20:00 |  | N |  |  |  |  | Blown transformer fuse P26 W Main St. Cause was burnt up cut out tap. ABB Order Id: 872899 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810341 | A
02/27/2026 07:19:55 | MECo | Bay State West | MONSON | STAFFORD RD | PALMER 503 | 09-503L2 | 15 | OH | 79 | 0 | 1.68 | 131.67 | 02/23/2026 13:31 | 02/23/2026 15:12 | Tree Contact | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 14:40 |  | N |  |  |  |  | Tripped B phase Cutout Mounted Recloser (1 of 3) P12 S Main St caused by tree limb P66 Stafford Rd. ABB Order Id: 872401 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810205 | A
02/26/2026 17:30:37 | MECo | Bay State West | CHARLTON | BURLINGAME RD | WEST CHARLTON 415 | 01-415L2 | 15 | OH | 153 | 0 | 2.39 | 364.65 | 02/23/2026 10:28 | 02/23/2026 12:51 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 12:30 |  | N |  |  |  |  | Blown line fuse P38 Burlingame Rd due to tree limb falling on Burlingame. ABB Order Id: 871861 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810183 | A
02/26/2026 17:09:28 | MECo | Bay State West | WORCESTER | HOLDEN ST | GREENDALE 24 | 01-24W2 | 15 | OH | 70 | 0 | 0.74 | 51.33 | 02/23/2026 09:46 | 02/23/2026 10:30 | Tree Contact | No failure or Unknown |  | WIND | M | N | Y | N | tc | 02/23/2026 10:15 |  | N |  |  |  |  | Blown line fuse P25 Holden St due to tree limb falling somewhere on Holden St. ABB Order Id: 871560 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810129 | A
02/26/2026 17:02:27 | MECo | Bay State West | WEBSTER | CUSHING RD | EAST WEBSTER 412 | 01-412L2 | 15 | OH | 39 | 0 | 3.12 | 121.55 | 02/23/2026 09:28 | 02/23/2026 12:35 | Tree Contact | Insulator - pin or post |  | WIND | M | N | Y | N | tc | 02/23/2026 10:30 |  | N |  |  |  |  | Blown line fuse at P9 Cushing Rd and blown transformer fuses at P1 Overlook Ave due to tree falling taking primary pin off pole P1 Overlook Ave. ABB Order Id: 871448 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810163 | A
02/26/2026 16:38:44 | MECo | Bay State West | WORCESTER | CRYSTAL BL HS 12 (0369) S ST | WEBSTER STREET 6 | 01-6J326 | 5 |  | 5 | 0 | 5.03 | 8.55 | 02/23/2026 06:51 | 02/23/2026 11:53 | Tree Contact | Conductors |  | SNOW | M | N | Y | N | tc | 02/23/2026 06:51 |  | N |  |  |  |  | Manually opened transformer fuse P10-82 Crystal BL HS 12 to make repairs to secondary. Tree took down backyard secondary to house 31 Richards St. ABB Order Id: 871871 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810148 | A
02/26/2026 16:33:24 | MECo | Bay State West | WORCESTER | HARLOW ST | FARADAY STREET 11 | 01-11J330 | 5 |  | 17 | 0 | 5.89 | 100.02 | 02/23/2026 13:06 | 02/23/2026 19:00 | Tree Contact | Transformer O/H conv. |  | RAIN | M | N | Y | N | tc | 02/23/2026 14:00 |  | N |  |  |  |  | Failed transformer P3 Harlow St due to tree. ABB Order Id: 872316 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810295 | A
02/26/2026 16:32:09 | MECo | Bay State West | SPENCER | BROOKS POND RD | MEADOW STREET 552 | 01-552L1 | 15 | OH | 64 | 0 | 0.33 | 21.33 | 02/24/2026 16:45 | 02/24/2026 17:05 | Tree Contact | No failure or Unknown |  | NORM | M | N | Y | N | tc | 02/24/2026 16:45 |  | N |  |  |  |  | Manually opened line fuse P0-50 Brooks Pond Rd for emergency repair to remove a fallen tree P23-50 Brooks Pond Rd from primary. ABB Order Id: 873805 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810714 | A
02/26/2026 16:23:42 | MECo | Bay State West | WARWICK | WENDELL RD | WENDELL DEPOT 705 | 09-705W3 | 15 | OH | 13 | 0 | 0.71 | 9.10 | 02/25/2026 12:48 | 02/25/2026 13:30 | Physical Interference / Other | No failure or Unknown |  | NORM | M | N | Y | N | tc | 02/25/2026 13:18 |  | N |  |  |  |  | Blown A and C phase line fuses (2 of 2) P28 Wendell Rd due to MVA P16 Wendell Rd. ABB Order Id: 874356 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811044 | A
02/26/2026 16:12:34 | MECo | Bay State West | SPENCER | HASTINGS-NORTH RD | MEADOW STREET 552 | 01-552L1 | 15 | OH | 79 | 0 | 1.23 | 97.43 | 02/23/2026 07:06 | 02/23/2026 08:20 | Tree Contact | Overhead Device Other |  | BLIZ | M | N | Y | N | tc | 02/23/2026 07:45 |  | N |  |  |  |  | Blown line fuse P106 New Spencer Rd due to tree taking primary off pin P44 Hastings North Rd. ABB Order Id: 871242 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810114 | A
02/26/2026 16:03:16 | MECo | Bay State West | LANCASTER | SEVEN BRIDGE RD | PRATTS JUNCTION | 01-225W1 | 15 |  | 4 | 0 | 2.39 | 9.53 | 02/24/2026 07:38 | 02/24/2026 10:01 | Failed Equipment | Tap |  | NORM | M | N | Y | N | tc | 02/24/2026 08:35 |  | N |  |  |  |  | Failed high side transformer cutout tap P22 Seven Bridge Rd. ABB Order Id: 873350 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810470 | A
02/26/2026 15:01:06 | MECo | Bay State North | ANDOVER | CHANDLER RD | WEST ANDOVER 8 | 14-8T2 | 25 | UG | 272 | 0 | 18.53 | 98.05 | 02/25/2026 09:33 | 02/26/2026 04:05 | Failed Equipment | Switchgear |  | SNOW | M | Y | Y | N | tc | 02/25/2026 10:00 |  | N |  |  |  |  | Tripped vacuum fault interrupters SWGR 17 and SWGR 15 Shattuck UCD caused by failed SW13 Tech Dr While testing sections of outage to isolate, Pole Top Recloser P159-2 Shattuck Rd locked out. Shattuck UCD was abnormal at time of lock out due to previous fault on the 8T2X cable so entire UCD was being carried on 8T2Y cable. Crews re-isolated condition and SCADA closed PTR. Pad 3 Tech Dr was out for duration. ABB Order Id: 874391, 874187, 874495 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8811117 | A
02/26/2026 14:06:06 | MECo | Bay State West | BARRE | PLEASANT ST | BARRE 604 | 09-604W4 | 15 | OH | 168 | 0 | 1.77 | 206.15 | 02/23/2026 09:27 | 02/23/2026 11:13 | Tree Contact | No failure or Unknown |  | WIND | M | Y | Y | N | tc | 02/23/2026 10:00 |  | Y | Robert Rogowski;James M. Sabourin; | Email (barrefire@townofbarre.com);Email (jsabourin@barremapd.us); |  |  | Tripped A and C phase cutout mounted reclosers P7 Pleasant St caused by tree on primary P68 Pleasant St. Crew opened B phase to clear tree de-energized. ABB Order Id: 871459 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810142 | A
02/26/2026 13:41:32 | MECo | Bay State West | BRIMFIELD | BROOKFIELD RD | LITTLE REST ROAD 516 | 09-516L1 | 15 | OH | 17 | 0 | 2.94 | 49.87 | 02/23/2026 09:13 | 02/23/2026 12:10 | Tree Contact | Crossarm |  | BLIZ | M | N | Y | N | tc | 02/23/2026 10:00 |  | N |  |  |  |  | Blown line fuse (2 of 2) P57 Brookfield Rd caused by tree that fell and damaged crossarm P14 Dix Hill Rd. ABB Order Id: 871387 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810152 | A
02/26/2026 08:23:54 | MECo | Bay State North | LAWRENCE | INMAN ST | SOUTH UNION ST 61 | 14-61L3 | 15 |  | 61 | 0 | 0.94 | 56.93 | 02/22/2026 12:48 | 02/22/2026 13:44 | Unknown | No failure or Unknown |  | NORM | M | N | Y | N | tc | 02/22/2026 13:30 |  | N |  |  |  |  | Blown transformer fuse P990 Inman St, no cause found. ABB Order Id: 869863 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810058 | A
02/26/2026 08:20:19 | MECo | Bay State North | SALEM | PIERCE AVE | RAILYARD 49 | 12-49W6 | 5 |  | 48 | 0 | 3.23 | 155.20 | 02/22/2026 03:01 | 02/22/2026 06:15 | Failed Equipment | Cable - XLPE - PE |  | NORM | M | N | Y | N | tc | 02/22/2026 03:01 |  | N |  |  |  |  | Manually opened P2748 Pierce to make secondary cable repairs in MH124 Bridge. ABB Order Id: 869843 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810044 | A
02/26/2026 07:26:01 | MECo | Bay State West | NEW MARLBORO | CLAYTON ML RVR RD | SHEFFIELD 8 | 09-1108W2 | 15 | OH | 16 | 0 | 4.00 | 54.67 | 02/22/2026 17:00 | 02/22/2026 21:00 | Physical Interference / Other | Pole - wood |  | NORM | M | N | Y | N | tc | 02/22/2026 17:45 |  | N |  |  |  |  | Blown transformer fuse P76 Clayton Mill River Rd due to MVA that broke pole at that location. Manually opened line fuse P83 Clayton Mill River Rd to replace pole de-energized. ABB Order Id: 869871 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810077 | A
02/26/2026 06:50:47 | MECo | Bay State West | NEW MARLBORO | CANAAN VALLEY RD | RISINGDALE 9 | 09-1109W1 | 5 | OH | 37 | 0 | 23.36 | 183.78 | 02/22/2026 21:42 | 02/23/2026 21:04 | Tree Contact | Pole - wood |  | NORM | M | N | Y | N | tc | 02/22/2026 22:51 |  | N |  |  |  |  | Tree fell and broke P35 Canaan-Valley Rd. Manually opened line fuse P21 Canaan-Valley Rd to make repairs. ABB Order Id: 872731 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810324 | A
02/24/2026 07:23:04 | MECo | Bay State North | BOXFORD | MAIN ST | WOODCHUCK HILL | 14-56L3 | 15 | OH | 565 | 0 | 4.42 | 2471.22 | 02/23/2026 11:43 | 02/23/2026 16:08 | Tree Contact | Recloser |  | WIND | M | Y | Y | N | tc | 02/23/2026 12:47 |  | Y | Warren Gould; | Email (wgould@town.boxford.ma.us); |  |  | Pole top recloser P304 Main St locked out due to broken tree limb on load bushings of head unit. Also found multiple sections of low Hendrix due to fallen trees. Manually opened line fuses P813 Middleton Rd to isolate broken P874 Middleton Rd due to high winds. Recloser was not communicating and could not be locally closed from control cabinet -- closed load break P1153 Middleton Rd. ABB Order Id: 872083 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810223 | A
02/24/2026 07:08:09 | MECo | Bay State West | WORCESTER | BELMONT ST |  | 01-HT39 | 15 |  | 3 | 0 | 8.53 | 8.78 | 02/23/2026 08:47 | 02/23/2026 17:19 | Physical Interference / Other | Transformer padmount |  | SNOW | M | Y | Y | N | tc | 02/23/2026 09:15 |  | N |  |  |  |  | Failed pad mount transformer P294 Market St due to MVA. Switched Seabury Heights SWGR onto alternate source then opened Belmont at HWY290 SWGR load break so crews could open -3 SWGR fuses de-energized to isolate failed pad. De-energized again after repairs were made to close fuses. ABB Order Id: 871250 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810245 | A
02/23/2026 15:45:38 | MECo | Bay State West | WORCESTER | PLANTATION ST | BLOOMINGDALE 27 | 01-27W2 | 15 | OH | 200 | 0 | 0.84 | 13.13 | 02/23/2026 14:40 | 02/23/2026 15:31 | Tree Contact | No failure or Unknown |  | SNOW | M | Y | Y | N | tc | 02/23/2026 15:15 |  | N |  |  |  |  | Blown transformer fuse P2 Oakhurst St due to large tree on primary. Manually opened pole top recloser P164 Plantation St to remove tree. ABB Order Id: 872508 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810209 | A
02/23/2026 10:47:49 | NanECo | Bay State South | NANTUCKET | WAUWINET RD | CANDLE STREET 101 | 04-101L2 | 15 | OH | 100 | 0 | 2.47 | 246.67 | 02/23/2026 02:18 | 02/23/2026 04:46 | Failed Equipment | Overhead Device Other |  | WIND | M | N | Y | N | tc | 02/23/2026 03:55 |  | N |  |  |  |  | Blown line fuse at P61 Wauwinet Rd caused by broken ridge pin at P16 Squam. ABB Order ID: 869937 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810094 | A
02/23/2026 09:17:58 | MECo | Bay State South | MILFORD | HIGHLAND ST | ROCKY HILL 336 | 05-336W3 | 15 |  | 7 | 0 | 1.97 | 13.77 | 02/22/2026 17:52 | 02/22/2026 19:50 | Physical Interference / Other | Pole - wood |  | NORM | M | N | Y | N | tc | 02/22/2026 18:25 |  | N |  |  |  |  | Manually opened transformer fuse at P90 Highland St for pole replacement caused by MVA. ABB Order Id: 869872 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810073 | A
02/23/2026 09:00:59 | MECo | Bay State North | LOWELL | VARNUM AVE | BOULEVARD 77 | 14-77L3 | 15 | OH | 1196 | 0 | 2.62 | 1584.23 | 02/23/2026 05:52 | 02/23/2026 08:29 | Failed Equipment | Recloser |  | WIND | M | Y | Y | N | tc | 02/23/2026 07:36 |  | Y | Greg Hudon;Shaun Woods; | Email (ghudon@lowellma.gov);Email (swoods@tyngsboroughma.gov); |  |  | 77L3 circuit breaker at Boulevard sub locked out. Cause: Failed head unit of pole top recloser P88 Pawtucket Blvd. Restored customers past P93-50 Varnum Ave on feeder tie, lifted taps and bypassed PTR then closed station breaker to restore. ABB Order Id: 870307 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810109 | A
02/23/2026 08:37:07 | MECo | Bay State West | WARE | PLEASANT ST | WARE 1 501 | 09-501L2 | 15 |  | 8 | 0 | 3.36 | 26.80 | 02/23/2026 04:18 | 02/23/2026 07:40 | Physical Interference / Other | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/23/2026 07:02 |  | N |  |  |  |  | Transformer fuse door dropped open P22 Pleasant St caused by plow hitting the pole. ABB Order Id: 869987 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810104 | A
02/23/2026 04:28:18 | MECo | Bay State West | OXFORD | DANA RD | NORTH OXFORD 2 | 01-406L4 | 15 | OH | 8 | 0 | 2.53 | 20.27 | 02/23/2026 00:57 | 02/23/2026 03:30 | Tree Contact | No failure or Unknown |  | SNOW | M | N | Y | N | tc | 02/23/2026 02:10 |  | N |  |  |  |  | Blown line fuse P39 Dana Rd. caused by fallen tree P39 Brown Rd. ABB Order Id: 869908 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810090 | A
02/22/2026 23:53:47 | MECo | Bay State West | GRANBY | CHICOPEE ST | FIVE CORNERS 527 | 09-527L1 | 15 | OH | 53 | 0 | 1.43 | 75.97 | 02/22/2026 21:57 | 02/22/2026 23:24 | Physical Interference / Other | Anchor and Guy |  | NORM | M | Y | Y | N | tc | 02/22/2026 22:53 |  | N |  |  |  |  | Blown C phase line fuse (1 of 2) P34 Chicopee St due to MVA P25 Chicopee St that sent broken guy wire into the primary. ABB Order Id: 869902 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810080 | A
02/22/2026 21:50:38 | NanECo | Bay State South | NANTUCKET | UNION ST | CANDLE STREET 101 | 04-101L7 | 15 | OH | 2700 | 0 | 1.12 | 855.07 | 02/22/2026 18:15 | 02/22/2026 19:22 | Failed Equipment | Splice |  | NORM | M | Y | Y | N | tc | 02/22/2026 18:17 |  | N |  |  |  |  | 101L7 circuit breaker locked out at Candle street substation, cause was a failed 600A T-Body splice in MH 0-3 Washington at Commercial St. Opened pole top recloser P17 Old South Rd, and closed PTR P53 Old South Rd restoring back half of feeder and Bunker Rd Sub. Opened PTR P2 Fairgrounds Rd and closed load break P1 Parker Ln restoring other back portion of feeder. Isolated getaway from substation at disconnects P11 Old South Rd and closed PTR Fairgrounds Rd restoring all customers. ABB Order Id: 869888 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810075 | A
02/22/2026 16:34:03 | MECo | Bay State South | SEEKONK | WOODWARD AVE | MINK STREET 7 | 05-7L1 | 15 |  | 8 | 0 | 1.42 | 11.20 | 02/22/2026 07:24 | 02/22/2026 08:49 | Animal | No failure or Unknown |  | NORM | M | N | Y | N | tc | 02/22/2026 07:50 |  | N |  |  |  |  | Blown transformer fuse P2512 Woodward Ave caused by animal contact. ABB Order Id: 869849 | Katelyn Rioux | Katelyn.Rioux@nationalgrid.com | 8810056 | A